## How to
This is a workbook to help you prepopulate the required forms for Central Office
Installation jobs.
1. Completely fill out the page named "General Info". This can be done by clicking on the tab
marked General info at the bottom of the workbook. This information will be populated on each
form, where indicated in this workbook. If some of the fields are not applicable, leave them blank.
2. Do not leave the info that is in there from a previous job.
3. Each form can be accessed by clicking on the appropriate tab at the bottom of the screen if
needed.
4. Preparing to email your workbook.
To delete forms that are not applicable to your job, click on the tab that contains the form.
Click on "Edit" on the top toolbar, click on "Delete Sheet". Once you have completed the workbook
and all of the appropriate forms are contained in the file, click on "Save as" and enter the BVAPP#
in the file name. Make sure the file is saving to the the shared folders as specified in the process so you
or your co-workers can easily retrieve the workbook and will know where it is contained.
DO NOT DELETE THE GENERAL INFO PAGE. THIS PAGE CONTAINS ALL OF THE DATA
AND LINKS FOR THE PRE-POPULATION OF THE FORMS WORKBOOK.
5. Printing (only if needed).
To print the entire pre-filled workbook, click on the "AA Coversheet" tab. Then click on the shift key
and click on the last tab of the workbook.
For collo jobs, the CLEC forms will need to be printed.
You can print multiple forms by clicking on the first tab you wish to print, the click on
the Control key and click on the tabs of any other form you wish to print.
For Power jobs, the Power forms may need to be printed.
You can print multiple forms by clicking on the first tab you wish to print, the click on
the Control key and click on the tabs of any other form you wish to print.
Once you have determined what forms you wish to print, click on File and then print or click
the little printer ICON on the top of the page.

## General info
Fields in RED must be completed by the WMC AA. Fields in Blue are Required for CLEC jobs and completed by the WMC AA. Fields in Black are filled out by the installer
Fireworks Project Number
Job Number (or BVAPP)
CLEC Name
CLEC location ID
CLLI
Address ID
Central office name
CO Address
City, State, Zip Code
Design Engineer
Design Engineer RC code
Design Engineer contact number
Installation Company
Installation Manager
Installation Manager phone number
Analytical Associate
AA Phone
AA Fax
WFA Ticket Number
Lead Installer
Installers Contact number
Electrical Vendor
Lead Electrician
Lead Electrician contact number
CO Authorized phone number
CO Authorized fax number
CO Staging location
CO Admin Location
CO Manager
CO Phone number
Scheduled start date
Actual start date
Walkthrough date
Scheduled completion date
Actual completion date
NCMS Number (if needed)
Job description of equipment added / removed
Equipment added, modified, removed location (s)
NMA number
Marked drawings
Scope Of Work/Desc:
Note on B6: Qwest: Please use capital letters
Note on B4: Qwest: Use only for Collo jobs
Note on B3: Qwest: This is the same as the BAN #and E. Number. Please use capital letters
Note on B5: Qwest: Please use capital letters
Note on B26: Qwest: Telephone number CO ops will let you use during installation
Note on B27: Qwest: Fax number CO ops will let you use, usually the CO fax number in that office.
Note on B28: Qwest: Location in CO where equipment to be installed is stored.
Note on B29: Qwest: Location where in CO where you perform paper work
Note on B38: The scope of work on this job.
Note on B39: Qwest: List the equipment added
Note on B41: Qwest: Insert Yes or No and if Yes, date sent to engineer.

## AA Coversheet
0
THIS JOB PACKAGE WAS PREPARED BY:
PREPARED BY:
0
PHONE:
0
FAX:
0
IN THE EVENT OF AN OUTAGE OR EMERGENCY CALL:
AZ,CO, ID, MT, NM, UT, & WY – 800-830-0722
IA, MN, ND, SD, NE, OR & WA – 800-341-8188
TO OBTAIN A PNAR (PLANNED NETWORK ACTIVITY NUMBER)
PLEASE CALL 1-800-258-8144
NMA Group Phone: 800-557-0778, Serial, Discrete, and Alarm Testing Option 1; X.25, CO-LAN Assg't/Provisioning Option 2 Fax: 612-663-3015
UPON COMPLETION OF THE JOB
PLEASE RETURN TO:
Work Management Center (WMC)
ATTENTION:
0
700 W. Mineral, Wyoming
Littleton, Co. 80120

## NAVL WAREHOUSES
0
PHOENIX,AZ | NAVPHAZ | TUCSON, AZ | NAVTUAZ
AMERICAN WESTERN DISTRIBUTION |  | DANIELS MOVING AND STORAGE
1511 S 47TH AVE. |  | 3135 S. DODGE BLVD
85403 |  | 85713 off 520-514-9007
KAREN BELLAR (602)-272-6016 X205 |  | SAMANTHA SEDRICK cell 520-270-3153
JOE VALENZUELA (602)-272-6016 |  | ERIC SCHWARTZ cell 520-225-8267
DENVER, CO. | NAVDECO | COLORADO SPRINGS, CO | NAVCOCO
CDG COLORADO DISTRIBUTION GROUP |  | ARROW MOVING & STORAGE
4725 LEYDEN, SUITE D 80216 |  | 2885 JANITELL ROAD EAST
1ST CONTACT DIRECT LINE 720-377-0523 |  | 80906
2ND CONTACT CRYSTAL ELKERTON 303-847-7232 |  | PAUL GREER (719)-527-0616
3RD CONTACT WENDI PORTMAN 512-731-6750 |  | SHELDON PERINO (719)-527-4822
GRAND JUNCTION, CO | NAVGRCO | CHEYENNE, WY | NAVCHWY
MESA MOVING AND STORAGE |  | BURKE MOVING AND STORAGE
681 RAIL ROAD BLVD |  | 388 NORTH AMERICAN ROAD
81505 |  | 82007
MARC THOMPSON (970)-242-1565 EXT.349 |  | BARRY RYERSE (307)-632-5536
TERRY KING (970)-242-1565 EXT 369 |  | BRYAN SCADDEN (307)-632-5536
CASPER, WY | NAVCAWY | BOISE, ID | NAVBOID
WYOMING TRANSFER |  | AIR VAN NORTH AMERICAN
330 SOUTH SPRUCE ST. |  | 12368 WEST MONSANTO STREET
82601 |  | 83713
CAROL (800)-711-3826 |  | DAWN URATA (208)-341-1088
JIM SEE (307)-259-0840 CELL, HM (307)-265-0956 |  | DAVE BOWMAN (208)-341-1081
POCATELLO, ID | NAVPOID | JOHNSTON, IA | NAVDEIA
LEE HAWKES TRANSFER |  | BELTMANN NORTH AMERICAN
848 SOUTH 1ST STREET |  | 5605 NORTHWEST 100TH ST.
83201 |  | 50131
KATHY ADAMS (800)-777-4395 |  | KELLY LEUTZINGER (515)-986-5559
BRYAN COOPER (208)-233-2337 |  | GREGG. (800)-398-5550
NORTH LIBERTY, IOWA | NAVIOIA | ST PAUL, MN | MANSTMN
HAWKEYE NORTH AMERICAN |  | BELTMANN NORTH AMERICAN
2870 STONER COURT |  | 2480 LONG LAKE ROAD
52317 |  | ROSEVILLE, MN 55113
JULIE KRETZSCHMAR (800)-397-3700 EXT. 230 |  | JOHN ROIGER (800)-949-8880 EXT. 2880
MICHELLE HUFF (319)-665-4020 EXT. 224 |  | GLENN WEAKLEY (651)-639-2910
BILLINGS,MT | NAVBIMT | MISSOULA, MT | NAVMIMT
KING TRANSFER |  | MONTANA TRANSFER COMPANY
7232 GRAND AVE. |  | 200 TRADE STREET
59106 |  | 59808
Gerrick Angel (406)-656-5464 |  | JARRET HOKE (800)-447-7557
ALLAN NICHOLS (406)-252-6394 |  | CLINT BAERTSCH (406)-728-8080
FARGO,ND | NAVFAND | BISMARK,ND | NAVBIND
FETTES MOVING AND STORAGE |  | JOBBERS MOVING & STORAGE
3939 7TH AVE |  | 1200 INDUSTRIAL DRIVE
58102 |  | 58501
ARLENE DITTUS (800)-325-3696 |  | JANICA SOBOT (701)-222-1111
DAVE GLASER (701)-277-3631 |  | CINDY TERNS (701)-222-1111
OMAHA, NE | NAVOMNE | ALBUQUERQUE, NM | NAVALNM
ACE STORAGE |  | ALBUQUERQUE MOVING & STORAGE CO
7820 L STREET |  | 5001 PASEO DEL NORTE NE
68127 |  | 87113
SCOTT VAUGHN (402)-593-1234 |  | LES SMITH 505-823-1441
KATHY WALKER (402)-593-1234 |  | JOE BACCA 505-823-1441
Page 1 of 2
0
EUGENE, OR | NAVEUOR | PORTLAND,OR | NAVPOOR
LILE NORTH AMERICAN |  | AIR VAN NORTH AMERICAN
3330 ROOSEVELT BLVD. |  | 119999 S.W. 95TH PLACE
97402 |  | TUALATIN 97062
SUE STRIBLING (541)-689-6683 |  | STEPHANIE BOETGER (800)-862-4801
BOB HIXSON (541)-683-3900 |  | AUTUMN MENDENHALL (503)-885-2353
PASCO, WA | NAVPAWA | MEDFORD, OR | NAVMEOR
AIR VAN NORTH AMERICAN |  | CUMMING TRANSFER
2440 E. AINSWORTH |  | 2061 LARS WAY
99301 |  | 97501
RANDY COX (800)-456-0925 |  | NITA LAMB (800)-866-9640
ERIC BENDER (509)-547-0528 |  | ED WELCH (541)-772-6278
SPOKANE, WA | NAVSPWA | SEATTLE, WA | NAVSEWA
LILE MOVING AND STORAGE |  | AIR VAN NORTH AMERICAN
E 7017 MISSION |  | 1500 INDUSTRY ST, STE 300
99212 |  | EVERETT 98203
TIM ORSBORN (800)-543-1554 |  | SANDY ARMBRUSTER 425-350-2177
DIANA DAUTER (509)-534-1554 |  | sarmbruster@airvan.net
RAPID CITY, SD | NAVRASD | SIOUX FALLS, SD | NAVSISD
GREENS MOVING & STORAGE |  | BROUWER RELOCATION
1115 EAST NEW YORK STREET |  | 3503 N. 1ST AVE
57701 |  | 57104
GAY WHALIN (605)-342-7060 |  | JARRED BROUWER (605)-333-0620
BRADY CHRISTOFFERSON |  | BRANDI MEYER (605)-333-0620
SALT LAKE CITY, UT | NAVSAUT
REDMAN VAN AND STORAGE
2589 S.2570 W.
WEST VALLEY CITY 84119
LYNN CHANDLER (800)-733-6261
DEBBIE SMITH (800)-733-6261
IF CONTACT CAN NOT BE MADE WITH NUMBERS
PROVIDED ABOVE, PLEASE CONTACT:
JEFF RYAN 303-599-1902 PAGER
OR JOHN RULLA 303-707-3111
Page 2 of 2

## Excess Warehouses
0
EXCESS MATERIAL WAREHOUSES
ARIZONA
AMERICAN WESTERN DISTRIBUTION
1511 S 47TH AVE.
PHOENIX, AZ. 85403
Contact: KAREN BELLAR
Phone: 602-272-6016 X205
Fax: 623-936-2683
COLORADO
A-1 Relocation
11701 E 33RD AVE.,
AURORA, CO. 80010
Contact: DANIEL HERNANDEZ
Phone: 303-364-2684 EXT. 5519
Fax: 303-364-0903
OREGON
Air Van North American
20141 SW 95th Place
Tualatin, OR 97062
Contact: ROBERT ADAMS
Phone: 503-380-0657
Fax: 503-885-2363

## Job Start Policy
0
Job Start Policy
1) Installation crews will complete the following “Job Start” functions no later than 3 calendar days after
the Work Package Materials Availability date. This is to occur even if there is insufficient material to actually start
the physical work on the job in order to identify and solve all potential installation problems early in the process.
2) Completing the “Job Start” function is defined as:
a) Verifying the installer has the latest Work Package (check IOT or NDS).
b) Identifying whether the job is feasible, as engineered, to include:
i) Determining that all cable-racking runs required to complete the job are not impeded.
ii) Determining that all cabling radius bends can be installed to 77350 standards.
iii) Determining that all assignments for power, signal, synch, etc. terminations are available.
iv) Determining that the materials ordered on the job spec allows the satisfactory completion of the job.
c) Identifying materials issues:
i) All materials ordered have been received by the installation crew, or have been verified to be available
at an off-site storage facility.
ii) This verification is not merely a check of a Procurement system. It is a physical check of as many of the
package contents as practical to ensure that the materials meet the job requirements and Job Finder
Report contents. The purpose is to identify engineering ordering or materials delivery problems as
early as possible.
iii) Examples (not meant to be all-inclusive):
(1) Actually open boxes to check packing slips vs. contents.
(2) Do not need to unravel cable reels to verify footage, but be aware as installation progresses.
(3) Check that BOM and packing slip and item itself are consistent.
(4) Check to see that panels that expand bay capacity are the correct type.
iv) Ensuring that any additional material needs are identified and ordered as soon as possible.
d) Identifying Real Estate items - (e.g Cable holes cut, Unistrut satisfactory, Collocation Cage placed, etc.)
e) Filling out and obtaining CO Operations’ signature on the General Method of Procedure. The MOP may be
posted in the Central Office, in the possession of the CO Ops Rep, or in the possession of the installer for
unstaffed locations.
f) When on-site construction actually commences and work on live network equipment is anticipated:
i) Ensure that a PNAR is opened using http://lno.uswc.uswest.com/cgi-bin/pnar/PNAR.pl
or by calling the appropriate center.
ii) Log the NCMS # in IOT.
3) Beginning the physical work on the job is required within 3 business days of posting the General Method
of Procedure (MOP) unless supported by a Date Management Root Cause code entered in IOT as a Job Start
note which explains the delay (see codes listed below).
4) COMMUNICATIONS - When the "Job Start" functions are complete:
a) IOT will be updated by filling out the IOT Electronic MOP with the following information
i) For Customer Premise jobs note who signed MOP (can be appropriate QTI Sup, Field Eng., DS Rep,
or CO Rep).
ii) For all other C.O. jobs:
(1) Note who signed the MOP.
(2) Note that the MOP is either posted or provided to CO Ops.
b) Notes of any issues uncovered during the above checks will be entered as needed and documented on
proper job forms (including who was contacted to resolve).
Root Cause Codes
1. PEG (Incorrect configuration)
2. Site Survey (Site survey incomplete or not done)
3. Planning (Standard intervals, Planning input incorrect)
4. Detail Engineering (Design issue, incorrect material ordered, drawings not updated or
incomplete, received unreasonable or incorrect dates)
5. Material (Damaged material, backorder, incorrect PID)
6. Installation (Resource issue, re-work issue)
7. Customer (Customer not ready)
8. Scheduling (Reschedule due to higher priority job, removed from hold)
9. Power (No power available)
10. Real Estate (Building not ready)
11. Business & Consumer Markets (formerly Central Office Operations)
12. WMC (Info late to field, job not assigned)
13. Quality (Pre-existing condition to fix, re-work due to request from quality) Note: Examples not all inclusive.
14. Weather
15. At Work Package release negotiated date.
16. Right Of Way (ROW) issues (radio jobs)

## Document Routing Checklist
0
DOCUMENTS TO OTHER DEPARTMENTS (QTI, WMC, Engineering, etc.) | In IOT | White Envelope | Sent in Elec Workbook
MOP/General & Detailed RG47-0005 & RG47-0162 (Posted MOP should be placed in Electronic Job Packet (EJP) | X | X | N/A
Job Log RG41-0046 | X | N/A | N/A
Material Shortage Form RG47-0166 (may need to fax or email copy to WMC during job) | N/A | N/A | X
Central Office Common Systems Order Form RG47-0165 (may need to fax or email copy to WMC during job) | N/A | N/A | X
Test Record(s) RG47-0157 | N/A | N/A | X
Job Information Memorandums (JIMS) RG47-0004 | X | N/A | N/A
Letter(s) Of Deviation (if issued) RG47-0169 (email electronic copy or fax to WMC along w/elec workbook) | N/A | N/A | X
Service Interruption / Degradation Report (if problem occurred) RG47-0013 | N/A | N/A | X
Installation Assignment & Capacity Sheet (Alarm sheet) RG41-0170 (still need to fax or email a copy to Alarm Center & Engineer) | N/A | N/A | X
Installation Revised / Completion Form RG47-0002 (If walkthrough occurs, place initialed copy in white envelope. If walkthrough doesn't occur, no need to put paper copy in white envelope) | X | X | N/A
Document & Material Disposition RG33-0043 (Installation may insert a copy in the (EJP) but it is not required) | N/A | N/A | X
Quality Checklist RG47-0161 | N/A | N/A | X
Certified Local Exchange Carrier (CLEC) Report RG47-0160 (must also leave copy in CLEC cage or posted at CLEC site) | N/A | N/A | X
Request for Disposition of Material RG47-0010 (Email or fax copy to WMC so engineer can determine disposition) | N/A | N/A | X
Bill(s) of Lading RG33-0017 (Keep copy in (EJP) | N/A | X | N/A
Marked Drawings (Scan one into the EJP, send 2nd copy to WMC if applicable) | N/A | X | N/A
Report of Equipment Disconnected from Plant RG47-0009 (Removal jobs only) | N/A | N/A | X

## RG33-0043 Material Disp
Document and Material Disposition
City, State |  |  | Office |  |  | FW Proj. No. |  | Job ID | Date
0 |  |  | 0 |  |  | 0 |  | 0
Job Type
IOF |  | XDSL/Megabit |  |  |  | Power |  | Collocation | Other
Line | Item No. | Quantity |  | √ | Description |  |  |  | Part No.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
Remarks:
Form Completed by: | [6 empty] | Material/Document Received by:

## RG47-0001 Storage Batt. Report
STORAGE BATTERY CHARGE RECORD AND END OF CHARGE REPORT
(Note: Use one set of forms per string and Ref. 77350, Chapter 10)
Page 1 of 2
JOB INFORMATION |  |  |  | BATTERIES AS RECEIVED OPEN CELL DATA | [7 empty] | BATTERIES AT TURNOVER (ON FLOAT)
(Note: Must be on float at least 24 hrs.)
|  |  |  | Cell # | SERIAL # |  | MFG. Date | Voltage | Specific Gravity | Acid Level |  | Cell# | Voltage | Temp Deg. F. | Specific Gravity | Voltage within 2.14V 2.27V
Plant ID:
String ID: | [15 empty] | (Y or N)
CENTRAL OFFICE |  | 0 |  | 1 | [7 empty] | 1
ADDRESS |  |  |  | 2 | [7 empty] | 2
0 |  |  |  | 3 | [7 empty] | 3
CITY & STATE |  |  |  | 4 | [7 empty] | 4
0 |  |  |  | 5 | [7 empty] | 5
SUPPLIER |  | 0 |  | 6 | [7 empty] | 6
SUPP. ORDER# |  |  |  | 7 | [7 empty] | 7
FIREWORKS# |  | 0 |  | 8 | [7 empty] | 8
JOB ID # |  | 0 |  | 9 | [7 empty] | 9
ADDRID |  | 0 |  | 10 | [7 empty] | 10
CLLI CODE |  | 0 |  | 11 | [7 empty] | 11
INSTALLER NAME |  | 0 |  | 12 | [7 empty] | 12
BATTERY MFG |  |  |  | 13 | [7 empty] | 13
BATTERY MODEL |  |  |  | 14 | [7 empty] | 14
CATALOG# |  |  |  | 15 | [7 empty] | 15
DATE RECEIVED |  |  |  | 16 | [7 empty] | 16
CHARGE BY DATE |  |  |  | 17 | [7 empty] | 17
TORQUE Value |  |  |  | 18 | [7 empty] | 18
PLANT Float Voltage |  |  |  | 19 | [7 empty] | 19
NOMINAL Float Voltage |  |  |  | 20 | [7 empty] | 20
TEMP.REF.CELL # |  |  |  | 21 | [7 empty] | 21
TURNOVER DATE |  |  |  | 22 | [7 empty] | 22
Turnover Avg. Voltage |  |  |  | 23 | [7 empty] | 23
ACCEPTED BY: |  |  |  | 24 | [7 empty] | 24
FOOTNOTES
| 1. Nominal float voltage is plant float voltage divided by the number of cells in the battery string | [8 empty] | 5. Batteries must be on float 24 hours. Before connecting to plant.
| 2. At turnover each cell must measure between -2.14V and -2.27V | [8 empty] | 6. Acid Level: check to see if the acid level is acceptable; if so mark O.K.
| 3. Accepted By: must be a Power Tech. Or COT/Supv. In charge | [8 empty] | 7. All measurements shall be rounded to the nearest 100ths digit
| 4. Temp.Ref.Cell will be selected as Defined in 77350, chapter 10 | [8 empty] | (Ex: 2.511V through 2.514V = 2.51V, and 2.515V through 2.519V - 2.52V)
STORAGE BATTERY CHARGE RECORD AND END OF CHARGE REPORT
(Note: Use one set of forms per string and Ref. 77350, Chapter 10)
Page 2 of 2 |  | 0
Plant ID:
String:
| {Cell Voltage readings for first 100 hrs. of charge} | [5 empty] | {Additional Hours of Charge as Needed}. |  |  |  |  | {End of Charge Readings}.
DAY | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | Volts | Specific Gravity | Temp
DATE
TIME
CELL#
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
Charger AMPS
Charger voltage
FOOTNOTES
1. Battery charger must be able to supply enough current and voltage to bring the string up to charge level. The charger shall be
at least 1/100th of the battery amp hr. rating. Example 4000 amp hr. batteries would require a min. 40 amp charger.
2. Charge level is when the (First) cell reaches 2.38V to 2.50V, per mfg. Requirements (Do not exceed 2.55 V on any of the cells
during this charge process). When this level is reached the 100 hours (minimum) of charge is started to bring all the cells up to this level.
3. End of charge readings are taken when:: Three consecutive hourly readings show each cell remains at its previous hourly reading,
while still on charge. Average charge level is ; the total of all cell readings divided by the number of cells in the batttery string.

## RG41-0046 Job Log
INSTALLATION JOB LOG
FIREWORKS #
0
DATE: | DETAILS:

## RG41-0170 Alarm Assgn, pg 1
0
INSTALLATION ALARM ASSIGNMENT AND CAPACITY SHEET #1
|  | Date Faxed: |  | Number of pages including cover sheet:
1. | To: NMA DATABASE |  |  | 2. | From: INSTALLER
| Name: |  |  |  | Name: | 0
| Phone #: 800-557-0778 Opt. 1 (Serial, Discrete) |  |  |  | Phone #:
| Fax #: 612-663-3015 |  |  |  | Page #: | 0
[5 empty] | Vendor Name: | 0
To: CENTURYLINK DESIGN ENGINEER
CLLI: ____________________________ BVAPP #: ____________________________ EST #: ____________________________
| Name: | 0 |  |  | CLLI: | 0
| Phone# |  |  |  | FW Proj. No. | 0
| Fax# |  |  |  | EST #: | 0
3. | IS THIS JOB AN ALARM ADDITION: |  |  | OR | REMOVAL:
4. |  |  | INSTRUCTIONS FOR COMPLETION
All jobs requiring alarms must be surveyed at Job Installation Start. The installer WILL be responsible for completing the Installation Assignment and Capacity Sheet and faxing (Cover page and all Assignment page(s)) to both the CenturyLink Engineer and the NMA Database Group, within a minimum of 48 hours up to a maximum of 72 hours of installation complete.
Before the job is completed the installer WILL be responsible for wiring and testing all Discrete and Serial alarms required with the NMA Database Group. After testing, NMA will issue a LOG #. Record LOG # on Installation Alarm Assignment & Capacity Sheet and on the RG-47-0002 (ICN - Installation Completion Notice). If there were alarms that could not be tested the Installer WILL fill out the Alarm / OSS Testing Incompletion Tag, including the NMA LOG #, and tie it onto the appropriate piece(s) of equipment. In the Capacity Note Section, located on Sheet 2, provide any information concerning capacity needs and / or requirements for future installations.
EXPLANATION OF FIELDS
| 1. | NMA Database Group and CenturyLink Engineer contact information to be supplied by Installer.
| 2. | Installer information (including job information) to be filled out by Installer completing the form.
| 3. | Designate whether this job adds alarms or removes alarms, NMA needs all information either way.
| 4. | Instructions for filling out the Installation Alarm Assignment and Capacity Sheets 1 and 2.
| 5. | Installer name, phone # (and/or page #), etc., to be filled in by the Installer before faxing.
| 6. | After testing record LOG #, issued by NMA.
| 7. | Capacity Notes are to be used to identify potential shortages in Discrete & Serial alarms, for
future growth.
| 8. | Alarm Bay is the Relay Rack location of the bay containing the alarm equipment.
| 9. | Shelf is the shelf designation for the alarm assignments.
| 10. | ETEL is the designation for the alarm assignments.
| 11. | Address/Remote (alarm).
| 12. | Additional Comments
| 13. | If alarms can not be tested; Fill out Alarm / OSS Testing Incompletion Tag; Attach (w/string) to
each piece of equipment (i.e. shelf). This may require more than (1) one Alarm / OSS Tag.
Note on F3: Qwest: put date in this cell
Note on D6: Qwest: Name of person you are faxing form to.

## RG41-0170 Alarm Sheet, pg 2
5. | Installer: | 0 |  |  |  | Phone #: |  |  | Pager #: | 0 |  | PIN# |  |  | Vendor |  | 0
| CLLI: | 0 |  |  |  | FIREWORKS # | 0 |  | JOB ID#: | 0
6. | LOG #: | [5 empty] | NMA Phone #: 800-557-0778 Opt 1 / NMA Fax #: 612-663-3015
7. | Discrete & Serial CAPACITY NOTES:
SERIAL ALARMS:
8. | Alarm Bay: RR |  |  |  |  | 8. Shelf: |  | 9. ETEL: |  |  | 10. Address/Remote(#)
ALARM UNIT INFORMATION
| MAP | MAC | PORT | DISPLAY# | SDR # | EQUIPMENT TYPE / RR / SHELF |  |  |  |  | TERMINAL |  | PUNCHING |  |  | LEAD XMT+ XMT- RCV+ RCV-
| Serial Alarms Tested By: | [7 empty] | Date:
DISCRETE ALARMS:
8. | Alarm Bay: RR |  |  |  |  | 8. Shelf: |  | 1.54 |  |  | 10. Address/Remote(#) |  |  | 31
|  |  | DATA BASE INFO |  | TERMINATING EQUIPMENT (NE) INFORMATION | [7 empty] | EQUIP X-CONN |  |  | ASSN X-CON
| SDR # | *BIT | Alarm Message |  | Equipment Type / RR / Shelf |  |  | Intfc Dwg | Figure | TS | Alm | Rtn | TB | Alm | Rtn | TB | Alm | Rtn
* Place a BIT/C in the BIT column if alarm is wired-out Normally Closed
| Discrete Alarms Tested By: | [7 empty] | Date:
12. | Additional Comments: |  |  | We will call tomorrow to figure out how we want to test working Eqpt.
13 | If alarms can not be tested; Fill out Alarm / OSS Testing Incompletion Tag; Attach (w/string) to each piece of equipment (I.e. shelf). This may require more than (1) one Alarm / OSS Tag.
NOTE: If more space is needed to record alarms use additional copies of this sheet / or attach blue line with all the appropriate information.
Note on C8: Qwest: This number need to be entered in the log also.

## JIM-ICN Categories Sheet
0
Categories Sheet
Job Extension Notice Categories (used as a part of the Date Management Process)
1. PEG (Incorrect configuration)
2. Site Survey (Site survey incomplete or not done)
3. Planning (Standard intervals, Planning Input information incorrect)
4. Detail Engineering (Design issue, incorrect material ordered, drawings not updated or incomplete,
received unreasonable or incorrect dates)
5. Material (Damaged material, backorder, incorrect PID)
5a. Material (Damaged/Defective)
5b. Material (Incorrect Material Ordered)
5c. Material (Lost/Stolen)
5d. Material (Materials haven't shipped/arrived)
5e. Material (Materail not ordered
5f. Material (Incorrect materials shipped)
6. Installation (Resource issue, re-work issue)
7. Customer (Customer not ready)
8. Scheduling (Reschedule due to higher priority job, removed from hold)
9. Power (No power available)
10. Real Estate (Building not ready)
11. Business & Consumer Markets Group (formerly Central Office Operations)
12. WMC (Info late to field, job not assigned)
13. Quality (Pre-existing condition to fix, re-work due to request from quality) Note: Examples not all inclusive.
14. Weather
15. At Work Package release negotiated date
16. Right of Way issues (radio jobs)
17. Testing (NMA or sync testing needed for job to be complete)
JIM Form Categories
A. This type of JIM would be entered by LPEC as a means of providing critical information to the engineer without an amendment or a change required in the IOT raking. Create a JIM but do not create an amendment.
B. This type of JIM would be entered by LPEC Construction if the job is in jeopardy of going over the IOT raked hours. Create a JIM & amendment - input # of hours in Qty field of the amendment using the "Misc" code. Use as much detail as possible for tracking purposes.
3. Electrical Contractor JIM – WMC AA creates a JIM but does not create an amendment unless Electrical Work was performed by LPEC. If LPEC performs the work, they will enter a JIM and create an amendment using the number of hours in the Qty field of the amendment and using the "Misc" code.
MD. Marked Drawings JIMs are entered by the WMC AA as a means of tracking the updates as submitted by QTI and entered in to COEFM by the engineer.
RG. RG47 JIMs are entered by the WMC AA as a means of tracking the progress of the RG47-0010 disposition of material form.
JIM Common Issues
Consumable Material - We do not pay for extra installation time for installing any consumable material.
Collocation Decommission Jobs - JIMs/Quotes must always be submitted to get the time necessary in IOT. Use JIM Category B, MISC Labor code. These JIMs should be submitted prior to the work beginning, if possible. If the Engineer has allocated X dollars in CPD, the AA would not be required to distribute the JIM.
Switch Quotes - JIMs/Quotes must be submitted by the WMC AA to get the time necessary in IOT when raking does not occur. Use JIM Category B and the appropriate Labor codes in the IOT amendment. These JIMs should be submitted prior to the work beginning.
AC Electrical Work - IOT does not rake for this work. If the work is done by Installation, create a JIM using Category 3 using the MISC labor code to recover the hours in IOT.
Items contained on BOM but not raked correctly - If an item is contained on the BOM but does not get raked by IOT, contact the WMC data team to ensure the part # is loaded into the catalog. When the job completes and the item has still not raked, insert a JIM using Category B and the appropriate Labor code.
Power Jobs - If appropriate raking does not occur, then QTI will use JIM Category B to document time in IOT. All JIMs for Power jobs will be distributed to the engineer.

## RG47-0002 ICN
Installation / Revised Completion Notice
Confirmation of Installation Completion
|  |  |  | Network Monitoring and Analysis (NMA) Confirmation # |  |  |  |  | 0 |  |  |  | Partial
Final
[6 empty] | NCMS # |  |  | 0
| Request for Revised Completion | [11 empty] | Extension
NCMS Closed Date
Marked Drawing, Date sent to WMC
Job-related materials & documentation handed over to CO Operations w/ signed RG33-0043.
Changed "Continuous Ship" address to immediate supervisor for materials borrowed from another job.
City, State, and Zip |  |  |  |  | Office / CLLI |  |  |  |  | Design Engineer's Name
0 |  |  |  |  | 0 |  |  | 0 |  | 0
FIREWORKS # |  | 0 |  |  | Job # | 0 |  |  |  | WFA # |  | 0
Scheduled Dates: | [5 empty] | Start | 0 |  |  | Complete |  | 0
Actual or Extension date: | [5 empty] | Start | 0 |  |  | Complete |  | 0
STRUCTURE | [14 empty] | Y/N/NA
Are the Frame/Bay/Cabinet top supports attached and secure?
Is the Frame/Bay/Cabinet grounded?
Are the Floor/Wall penetrations designated and fire stopped? (List holes used) Fire block Label (RG47-0133)?
Is the Illumination adequate?
Are the AC conduits and outlets located per specification (Typically front & rear of every first/last and 3rd bay)?
Are the combustibles and excess material cleaned up?
EQUIPMENT |  |  |  |  | LOCATION (RR, Shelf, block, jack, etc.) |  |  |  |  | Tested Y/N/NA |  |  | Designated Y/N/NA
Bay / Equipment Added
BDFB / PBD / Fuse Panel
DS0 MDF Vertical / Horizontal
DSX-1
DSX-3
Fiber Cables
Synchronization Cables
Alarm Cables
COLAN cables
Other
Job Package (All references in TP 77350 Issue M, Chapter 13.4)
Design Work Package (DWP) |  |  |  |  | Release # |  |  |  |  | Date:
Circuits and cables tested?
Has equipment that has been removed been noted on RG47-0009 & RG47-0010 and forms placed in job pack?
Job Comments: (Please refer to RG33-0043 for documents turned over to CO Operations)
Service Supplier Company |  |  |  |  | 0 | [5 empty] | Date
Installer Printed Name |  |  |  |  | 0 | [5 empty] | Telephone |  | 0
Installer Signature
For CenturyLink Use Only
This is: |  |  |  |  | Accepted |  |  | Not Accepted
If NOT Accepted, Reasons:
B&C Representative Printed Name | [6 empty] | 0 |  |  |  |  | Date
B&C Representative Signature | [11 empty] | Telephone |  | 0
Note on Q25: Qwest: Fill in all blocks with an Y, N or NA

## RG47-0004 JIM
Job Information Memorandum
Date
City, State and Zip | [5 empty] | Office | [7 empty] | Fireworka Project No. |  | JIM No.
0 | [5 empty] | 0 | [7 empty] | 0
Service Supplier Company Name
0
Subject
Work Pkg./Spec. Item Number
Confirming Telephone Call
From Installer | 0 |  |  |  | To Engineer |  | 0 | [7 empty] | Date
Drawing Change Req | [7 empty] | Job Cost Affected
|  | Yes | No | [5 empty] | Yes |  |  | No
Additional Material Req | [7 empty] | New WP release req
|  | Yes | No | [5 empty] | Yes |  |  | No
Problem Description
Suggested Remedy
[9 empty] | Total Hours: |  |  |  |  | Total Cost:
Effect on Job Completion Date
Submitted By: | [10 empty] | Telephone No.
Address | [10 empty] | Email Address
|  |  |  | State | [5 empty] | Zip Code

## RG47-0005 General MOP
Method of Procedure
COE Installation / Removal / Modification
Service Assurance Contact Numbers: |  |  |  |  | General MOP | Detail MOP
1-800-830-0722 NROC & Alarm Center |  |  |  |  | 1-800-341-8188 Switch/Sw Pwr.
1-800-258-8144 Net Facility Center |  |  |  |  | 1-800-879-1200 Net Event Management Ctr.
Service Assurance Power Contact No.: 1-800-713-3666
City, State | 0 | Office | 0 | Office Location | 0 | Phone
List Days and Hours of Operation |  |  |  | Start Date | 0 | Completion Date | 0
FW # | 0 | JOB ID | 0 | WFA# (if applicable) | 0 | Supplier/Vendor Name | 0
System Type (Refer to RG47-0162 for Power Switch Detailed MOPs) Switch | [5 empty] | Type
Toll |  | Collo |  | Fiber |  | Real Estate
DSL |  | Radio |  | Power |  | Other
Review the steps listed and place Y, N or NA in the appropriate box for the job. Work should not begin until this form has been reviewed and signed by CenturyLink and supplier representatives. All information must comply with CenturyLink Technical Publication 77350
STEP |  |  | DESCRIPTION |  |  |  | CO Ops | Installation
1 | A signed Method of procedure (MOP) shall be on site, reviewed and posted. The Question your Work Policy and Have You Considered Checklist has been reviewed.
2 | Have you reviewed the CenturyLink Supplier Expectations: Access & Security Chapter 2.2 Safety Chapter 2.4, Combustibles Chapter 2.6 TP 77350 on site and available?
3 | All tools and material will be staged/stored at __________________________________________(list location)
4 | The Work Package (WP) is on site and deemed feasible. All assignments are correct, ie. AC and DC Power systems, Grounding, Signal, Synchronization, DS0, DS1, DS3 Fiber and Alarm or Design Engineer has been contacted to correct per field conditions.
5 | All cable racks are sufficient and of the correct type. Cable routes, including entrances to the job associated equipment frames, are available and unimpeded.
6 | The material will be inventoried for correct quantities and types. Any Bill of Material (BOM) shortages will be identified, ordered and set with acceptable delivery dates for on time job completion.
7 | A separate Detail MOP will be completed for all work performed on live equipment whether presently in service or not. This includes work on equipment in an area where potential hazards exist. (A job order may have a number of Detail MOPs. Please see Tech pub 77350 15.3.1)
8 | Alarms will be verified, tested or non-test tagged attached to network element.
9 | Office drawings will be marked to reflect current office conditions.
10 | Applicable job papers, specs, documents, and parts will be signed over to CenturyLink representative.
11 | Surplus materials and supplier tools will be removed from the job site upon job completion.
12 | AC outlets and equipment lighting have been correctly engineered and provisioned as required.
13 | Real Estate items are complete, ie. Collocation cages, cable holes and other associated building changes.
14 | All material and engineering issues will be escalated to the WMC or Construction Program Administrator for the area.
JOB DESCRIPTION - please attach an additional piece of paper if necessary |  |  |  |  | FPIN NCMS |  | NCMS | 0
0
EQUIPMENT LOCATION |  |  |  | ALARM
POWER |  |  |  | AI X.25
DSX-1 |  |  |  | TIMING
DSX-3 |  |  |  | FIBER
MDF |  |  |  | MISC
The undersigned approved the procedures herein described as complete, whether a general or detailed procedure. No changes shall be made without approval of both the CenturyLink B&C representative and the Installation Supplier Representative or Contract agent.
Name (print & Signature) |  |  | Title | Contact Numbers
Person Performing/In Charge of Work (Required) |  |  |  | 24Hr Emergency Contact Number |  |  | Date
0 |  |  |  | 0
Real Estate or Service Supplier Representative |  |  | (Required) | Phone |  |  | Date
0 |  |  |  | 0 |  |  | B&C
Manager or Design Representative |  |  | (Required) | Phone |  |  | Date
0 |  |  |  | 0
B&C ON CALL Support Technician |  |  |  | Phone |  |  | Date

## RG47-0005 CLEC General MOP
CLEC GENERAL Method of Procedure
COE Installation / Removal / Modification
Service Assurance Contact Numbers: |  |  |  |  | General MOP | Detail MOP
800-830-0722 NROC & Alarm Center |  |  |  |  | 800-341-8188 Switch/Sw Pwr.
800-258-8144 Net Facility Center |  |  |  |  | 800-879-1200 Net Event Management Ctr.
Service Assurance Power Contact No.: 1-800-713-3666
City, State | 0 | Office | 0 | Office Location | 0 | Phone
List Days and Hours of Operation |  |  |  | Start Date | 0 | Completion Date | 0
BAN |  | JOB ID | 0 | WFA# (if applicable) | 0 | Supplier/Vendor Name | 0
System Type (Refer to RG47-0162 for Power Switch Detailed MOPs) Switch | [5 empty] | Type
Toll |  | Collo |  | Fiber |  | Real Estate
DSL |  | Radio |  | Power |  | Other
Review the steps listed and place Y, N or NA in the appropriate box for the job. Work should not begin until this form has been reviewed and signed by CenturyLink and supplier representatives. All information must comply with CenturyLink Technical Publication 77350
STEP |  |  | DESCRIPTION |  |  |  | CO Ops | Installation
1 | A signed Method of procedure (MOP) shall be on site, reviewed and posted. The Question your Work Policy and "Have You Considered Your Work" Checklist has been reviewed.
2 | Have you reviewed the CenturyLink Supplier Expectations: Access & Security Chapter 2.2 Safety Chapter 2.4, Combustibles Chapter 2.6 TP 77350 on site and available?
3 | All tools and material will be staged/stored at __________________________________________(list location)
4 | The Work Package (WP) CenturyLink is on site and deemed feasible. All assignments are correct, ie. AC and DC Power systems, Grounding, Signal, Synchronization, DS0, DS1, DS3 Fiber and Alarm or Design Engineer has been contacted to correct per field conditions.
5 | All cable racks are sufficient and of the correct type. Cable routes, including entrances to the job associated equipment frames, are available and unimpeded.
6 | The material will be inventoried for correct quantities and types. Any Bill of Material (BOM) shortages will be identified, ordered and set with acceptable delivery dates for on time job completion.
7 | A separate Detail MOP will be completed for all work performed on live equipment whether presently in service or not. This includes work on equipment in an area where potential hazards exist. (A job order may have a number of Detail MOPs. Please see Tech pub 77350 15.3.1)
8 | Alarms will be verified, tested or non-test tagged attached to network element.
9 | Office drawings will be marked to reflect current office conditions.
10 | Applicable job papers, specs, documents, and parts will be signed over to CenturyLink representative.
11 | Surplus materials and supplier tools will be removed from the job site upon job completion.
12 | AC outlets and equipment lighting have been correctly engineered and provisioned as required.
13 | Real Estate items are complete, ie. Collocation cages, cable holes and other associated building changes.
14 | All material and engineering issues will be escalated to the WMC or Construction Program Administrator for the area.
JOB DESCRIPTION - please attach an additional piece of paper if necessary |  |  |  |  | FPIN PNAR |  | PNAR | 0
0
EQUIPMENT LOCATION |  |  |  | ALARM
POWER |  |  |  | AI X.25
DSX-1 |  |  |  | TIMING
DSX-3 |  |  |  | FIBER
MDF |  |  |  | MISC
The undersigned approved the procedures herein described as complete, whether a general or detailed procedure. No changes shall be made without approval of both the CenturyLink B&Crepresentative and the Installation Supplier Representative or Contract agent.
Name (print & Signature) |  |  | Title | Contact Numbers
Person Performing/In Charge of Work (Required) |  |  |  | 24Hr Emergency Contact Number |  |  | Date
0 |  |  |  | 0
Real Estate or Service Supplier Representative |  |  | (Required) | Phone |  |  | Date
0 |  |  |  | 0
C O Operations Manager or Design Representative |  |  | (Required) | Phone |  |  | Date
0 |  |  |  | 0
Central Office Operations ON CALL Support Technician |  |  |  | Phone |  |  | Date
NOTE: B&C REP - UPON COMPLETION OF THIS FORM - FAX TO Work Management Center at 303-707-9082

## RG47-0009 Rpt of Dis
Report of Equipment Disconnected From Existing Plant
|  |  |  | Date: | Sheet __1____ | of ___1_______
Design Engineer's Name |  |  | Address |  | Partial | Final
0 |  |  | 0
City, State, Zip |  |  | Office | FIREWORKS Proj. No. | Job ID
0 |  |  | 0 | 0 | 0
| Quantity | Code | Description | Name of Circuit and Location From Which Disconnected. |  | Date Disconnected
| A | B | C | D |  | E
1
2
3
4
5
6
7
8
9
10
11
12
13
14
Service Supplier Representative |  |  |  | * Note complete form and place in job package for auditing
purposes.
Note on G23: Qwest: date form is completed
Note on I29: Qwest: actual date equipment was disconnected

## Material Review Form
| Date: |  |  | User Complete the form (Green Areas Required) Send Completed MRF to: Asset_RecoveryandDisposition@CenturyLink.com |  |  |  | Activity #:
|  | Name |  | Address | City | State | Zip | Phone # |  | Email
Originator:
Program Mgr/Planner
Site Contact:
| Physical Loc of Material | Enter Office, Site or CLLI Code here | [5 empty] | Disposition Approval:
| WBS / BVAPP: |  |  | Company Code: |  |  | WBS Element or Cost Center for Transportation Cost:
| Original PO #: |  |  | Plant Code:
Originator Comments:
AR&D Comments / Instructions:
| MFG. Name | Material Code or HECI | MFG. Part # | Part Description |  | Qty | UOM | Retired? Y/N | Cond. Code | Disposition: AR&D Use Only
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
Note on I6: Disposition Approval= If material is being allocated to the asset disposition process the appropriate manager's (Expenditure and Fiscal Approval Authorities) based on approval is required.
Note on B7: WBS / BVAPP = WBS Element (i.e. E.######.C01), BVAPP, Job Number, Work Activity or Project Number for removal of material.
Note on E7: Company Code: Can be obtained by Logging on to SAP Portal - Select Material Mgmt tab, Select the Plant/Vendor/Address Search tab to find your Company Code, begins with a T, S or E and 3 digits (i.e. T861, S900, E001).
Note on B8: Original PO# (for Vendor Returns Only)= SAP PO, PeopleSoft PO or AMMS PO that the material will be returned to the vendor on.
Note on E8: Plant Code = Can be obtained by Login on to SAP Portal - Select Material Mgmt tab, Select the Plant/Vendor/Address Search tab to find your Plant Code (4 digits)
Note on J12: Condition Codes: Vendor Returnable: For material that is in Vendor Returnable Condition, New: For material that is new but never installed, Used: If the condition of the assets used but good condition for returning the asset to inventory, Defective: If the asset is defective not useable.

## RG47-0010 Disp of Material
CENTURYLINK REQUEST FOR PICK-UP AND REMOVAL OF SCRAP MATERIAL & JOB-RELATED PACKING
Date
Ship To Location |  |  |  | Street Address | City, State, Zip
Design Engineer's Name |  |  | Design Engineer Fax# | Job Site Address | City, State, Zip
0 |  |  |  | 0 | 0
Design Engineer Tel No. |  |  |  | On-Site Contact (Requestor) |  |  | Phone
|  |  | 0 | 0
Job ID or Cost Center |  |  | FIREWORKS PROJECT#
0 |  |  | 0
Please Note: Is there an MRF associated with this logistics request? |  |  |  |  | Y N
| Quantity |  |  | Brief Material Description | Reason For Return
| A | B | C | D | E | F | G | H | I
1
2
3
4
5
6
7
8
9
10
Column E and place a checkmark in the appropriate disposition Columns for each items (Columns A,D & E)
NOTE TO FORM ORIGINATOR: Fax or email form to: 1) A1 Logistics Customer Service Center Operations (303) 484-5796 or email to RG47@everywarehouse.com
Retain a copy to in the job package.
To Be Completed By Warehouse
Name of Receiver | Brief Material Description D: Phone; Reason For Return I: Date
ATTACH A COPY OF THIS FORM TO EACH BOX BEFORE RETURNING
0
Instructions for completing RG47-0010:
IMPORTANT: EACH FIREWORKS PROJECT NUMBER REQUIRES A NEW FORM TO BE COMPLETED.
1. Complete the top portion of the form with information pertaining to the job, contact information and the location where the material/equipment will be shipped.
2. Input the following information about the material/equipment being returned as follows (each item is recorded on a separate line):
Column A – Input the Unit of Measure (quantity and length)
Column D – Input the Material/Equipment Description (or reference the Bill of Material [BOM] item number and attach a highlighted/marked copy of the BOM to the form.)
Column E – Input the appropriate Return Code (list below line 10)
3. Distribute the form (email or fax) as appropriate, using the instructions at bottom of the form. (Most forms will be faxed to 303-484-5796 - warehouse)

## RG47-0013 Svc. Degradation Rpt
0
Service Interruption / Service Degradation Report
To: |  |  | Location:
Office | City | State | Fireworks Proj. No.
0 | 0 |  | 0
Time & Date Reported |  | Time & Date Cleared
Type of Equipment |  | MOP Completed/Approved? ____Yes ____No
Description of Service Interruption:
Corrective Action Taken:
Service Supplier Company Name |  | Telephone #
Service Supplier Rep Signature: |  | Date:

## RG47-0132 Cable Hole Label
| CABLE HOLE OPENED |  | RG 47-0132
| This hole is to be temporarily closed at the end |  | (5-15)
of each working day or when no additional cable
is to be run that same day and shall conform to
CenturyLink Technical Pub 77350
Project Number:
Vendor/Organization:
Date Closed:
Firestop Manufacturer:
UL Listed Fire Assembly or EJ number:
Responsible Party Contact Information:
RG 47-0132 Cable Hole Open Label 3"T X6"L
| FIRESTOPPED CABLE HOLE NOTICE |  | RG 47-0132
(5-15)
This cable hole has been firestopped in accordance
with CenturyLink Technical Publication 77350
Project Number:
Vendor/Organization:
Date Closed:
Firestop Manufacturer:
UL Listed Fire Assembly or EJ number:
Responsible Party Contact Information:
RG 47-0133 Firestopped Cable Hole Label 3"T X6"L

## RG47-0157 Test Record
TEST RECORD
DATE
FIREWORKS NO. | JOB ID |  | CLLI |  | OFFICE NAME |  | City & State
0 | 0 |  | 0 |  | 0 |  | 0
TEST EQUIPMENT USED |  | TYPE CIRCUIT
|  | DS-0 | DS-1 | DS-3 | Alarms | Power | Timing
FROM (ex: MDF, RR & Shelf) |  | TO (ex: MDF, RR & Shelf) |  |  |  | LEAD ID / DEFECT TYPE/ CORRECTED (Y/N)
DS-0
DS-1
DS-3
Alarms
Power
Timing
Fiber
INSTALLATION SUPPLIER |  | INSTALLERS NAME(S) (PRINT) |  |  |  | CONTACT NUMBER(S)
0

## RG47-0158 Fiber Test Record
FIBER OPTIC CABLE TEST RECORD
DATE |  | FIREWORKS NO. |  | JOB ID |  | CLLI |  | OFFICE NAME |  |  | CITY/STATE
TYPE OF TEST EQUIPMENT USED
EXFO FLS-300 |  | EXFO FPM-302X |  | AFL/NOYES VFI-2 |  | AFL/NOYES VOS3-00-0905 |  |  | FCP1-00-0910 FIBER CLEANING KIT
FROM: Frame Type: (e.g.; FDF, NGF, NG3, FMT or misc FDP) |  |  | TO Frame Type: (e.g.; FDF, NGF, NG3, FMT or misc FDP) |  |  | DEFECTS NOTED? Y N |  |  | CONDITION CORRECTED? Y N
[6 empty] | CABLE CATALOG NO. |  |  | CABLE SERIAL NO. |  | MFG. JOB NO.
PERFORMANCE SHEET - Pre-Installation (uncrated cable) Insertion Loss @1550nM
SUBUNIT | FIBER OPTICAL LOSS MEASUREMENT READINGS - (measured to and within + 0.5 dB)
| BLUE | ORANGE | GREEN | BROWN | SLATE | WHITE | RED | BLACK | YELLOW | VIOLET | ROSE | AQUA
1
2
3
4
5
6
PERFORMANCE SHEET - Post-Installation (cable run & secured) Insertion Loss @1550nM
SUBUNIT | FIBER OPTICAL LOSS MEASUREMENT READINGS - (measured to and within + 0.5 dB)
| BLUE | ORANGE | GREEN | BROWN | SLATE | WHITE | RED | BLACK | YELLOW | VIOLET | ROSE | AQUA
1
2
3
4
5
6
INSTALLATION SUPPLIER |  |  | INSTALLER'S NAME(S) (PRINT) | [5 empty] | CONTACT PHONE NO.
CTL CONTRACT VENDOR

## AC Elec Quote Form
AC Electrical Work Quote Form
Date | _____________________________________________________________
FIREWORKS # | 0
Installation Supplier(if not CTL)
Contact
Phone
Contact
Phone
CenturyLink Engineer/Planner |  | 0
Phone
CenturyLink Installer |  | 0
| Phone | 0
Description of work performed e.g. placing/removing AC outlets,
lighting, junction boxes, AC runs, etc:
CenturyLink Central Office |  | 0
(CLLI code and state) |  | __________________________________________________
Estimated Complete Date |  | __________________________________________________
Labor $ | _____________________________________________________________
Hours | _____________________________________________________________
Rate/per hour $ | _____________________________________________________________
Material (if applicable) $ |  | __________________________________________________
Detailed Material List - Please attach a list of Electrical Vendor provided material and CenturyLink provided
material (if applicable). Included in the Material List needs to be; line item detail, quantities and unit
prices for each part.
FAX TO: 303-707-9151 EMAIL: WMC.Team@CenturyLink.com

## RG47-0160 CLEC Power
CLEC POWER ASSIGNMENTS
OFFICE |  | 0
FIREWORKS PROJECT NO. |  | 0 |  | ICA # | 0
CLEC Company & Contact: |  |  |  | Decommission
CLEC Location ID: |  | 0
CLEC COMPANIES LOAD A
FROM-CenturyLink
BDFB/PBD Location | Shelf | Fuse/Brkr Position | Fuse/Brkr Amps | Cable Length (top to top) | Quantity of runs | Cable Size
CLEC COMPANIES LOAD B
FROM-CenturyLink
BDFB/PBD Location | Shelf | Fuse/Brkr Position | Fuse/Brkr Amps | Cable Length (top to top) | Quantity of runs | Cable Size
Contacts: Company and/or Name (24 Hour) | [6 empty] | Telephone #
Installation Supplier: |  | 0 |  |  |  |  | 0
CenturyLink Operations:
Fuses turned over to:

## RG47-0160 CLEC Sync
CLEC SYNC ASSIGNMENTS
OFFICE | 0
FIREWORKS PROJECT NO.: | 0 | ICA # | 0
CLEC Company & Contact: |  | Decommission
CLEC Location ID: | 0
CLEC COMPANIES PRIMARY
FROM-CenturyLink
Relay Rack Location | Shelf | Slot Position | Port
CLEC COMPANIES SECONDARY
FROM-CenturyLink
Relay Rack Location | Shelf | Slot Position | Port
Contacts: Company and/or Name (24 Hour) |  |  | Telephone #
Installation Supplier: | 0 |  | 0
CenturyLink B&C:
For Synch Leads: Termination/Unplugged:

## RG47-0160 CLEC DSO
CLEC DS0 CIRCUITS
Office |  | 0
FIREWORKS PROJECT NO.: |  | 0 |  |  | ICA # | 0
CLEC Company & Contact: |  |  |  |  | Decommission
CLEC Location ID: |  | 0
Cable Designation |  | DSO Vertical Location MDF/ICDF |  | Pair Count | Comments/Cable Slack (for decom only) | Cable Mined? Y/N (for decomm only)
DSO LINE SHARING ONLY (Data Only)
Cable Designation | DSO Vertical Location MDF/ICDF |  | Pair Count | Splitter Location (RR/Shelf or MDF/Block Location | Comments/Cable Slack (for decom only | Cable Mined? Y/N (for decomm only)

## RG47-0160 CLEC DS1
DS1 Circuits
Office |  | 0
FIREWORKS PROJECT NO.: |  | 0 |  | ICA # | 0
CLEC Company & Contact: |  |  |  | Decommission
CLEC Location ID: |  | 0
Cable Designation | Circuits Cable Count | RR | Panel | Jacks | Cable Slack Length (for decom only) | Cable Mined? Y/N (for decom only)
CLEC Relay Rack Location:

## RG47-0160 CLEC DS3
DS3 Circuits
Office |  | 0
FIREWORKS PROJECT NO.: |  | 0 |  | ICA # | 0
CLEC Company & Contact: |  |  |  | Decommission
CLEC Location ID: |  | 0
Cable Designation | Circuits Cable Count | RR | Panel | Jacks | Cable Slack Length (for decom only) | Cable Mined? Y/N (for decom only)
CLEC Relay Rack Location:

## RG47-0160 CLEC Fiber
CABLES FROM CENTURY LINK FIBER BAY TO CLEC EQUIPMENT
Office |  | 0
FIREWORKS PROJECT NO.: |  | 0 |  | ICA # | 0
CLEC Company & Contact: |  |  |  | Decommission
CLEC Location ID: |  | 0
Cable Designation | Circuits Cable Count | FDF RR | Panel | Ports | Cable Slack Length (for decom only) | Cable Mined? Y/N (for decom only)
CLEC Relay Rack Location:

## RG47-0161 Quality Checklist
FIREWORKS PROJECT NO.: | CLLI CODE:
0 | 0
DESIGN ENGINEER: | ENGINEER RC CODE:
0 | 0
ITEM TO CHECK | CORRECT? (NA, Y, N) | REMARKS
IRON -
1. Stanchion / Support per standards and configuration? 3.1.7, 3.13.6
2. Cut even and filed smooth? 3.13
- cut ends painted? 3.13.4
3. Bolts and nuts secured? 3.5
4. Lock washers in EQ Heavy areas? 3.9.2
5. Alignment correct? 3.13
6. Finish Clip / Cap in place? 3.4, 3.6
7. Splices / Clamps correct? 3.9.3
8. Cable rack labeled? 8.17
9. Other
BAY -
1. Top support - 2 supports bays, 4 supports cabinets? 3.12.2
2. Preloaded bays are wired correctly, within standards, and match front equipment drawings? 3.13.1
3. Bay ground is correct type and guage, crimped and connected correctly with star washers? 11.3
4. Bay label correct (RG47-0130 or RG47-0131)? 8.1
5. RR designation per standards and configuration? 8.3.1
6. Anchors torqued & Indicators in place or note in job log? 3.21
7. Molding / Dust shield attached? 77351 Chapter 2, Anchoring 2.5.6
8. End shield, end guards (If applicable)? 3.12.7
9. End of aisle labeled (both ends)? 8.3.6
10. AC outlets/lighting installed per standard ? 9.1
11. AC outlets/lighting labeled with fuse box and fuse position? 8.7.1 & 8.7.2
12. Other
EQUIPMENT -
1. Location / Alignment (per Floor Plan, aisle spacing F&R, guards req'd)? 3.16.1
2. Bolts, nuts, screws tightened? 3.5
3. Correct amount of supports? 3.16.2
4. Grounding (chassis/frame) of correct type and guage, crimped and properly connected with star washers? 11.1.8
5. Shelf / Equipment labeling correct per standards and configuration, (ie F/E drawing, RG47-0130) 8.3.
6. Other
CABLE INSTALLATION POINT TO POINT - (Maintenance slack loop not to exceed 4 feet. 5.1)
- DSO -
1. Type & gauge correct? Per DWP and standards
2. Termination location correct both ends? Per Work Package
3. Routing correct? 5.1
4. Protection of wire? 5.4
5. Spliced per standard? 5.13
6. Connections
- amphenols seated correctly and secured? 7.3
- wire wraps correct? 7.7
7. Securing : -
- cable lacing secure & correct? 5.5
8. MDF and Blocks labeled correctly? 8.5
9. Shields/Drain leads correct? 7.7
10. Bending radius correct? 5.3
11. Tested? 2.8
12. Other
- DS1 -
1. Type & gauge correct? Per DWP and standards
2. Termination location correct both ends? Per Work Package
3. Routing correct? 5.1
4. Protection of wire? 5.4
5. Spliced per standard? 5.13
6. Connections:
- amphenols seated correctly and secured? 7.3
- wire wraps correct? 7.7
7. Securing
- cable lacing secure & correct? 5.5
- Shelf/panel labeled correctly? 8.3
8. Shields/Drain leads correct? 7.7
9. Bending radius correct? 5.3
10. Tested? 2.8
11. Other
- DS3 -
1. Type & gauge correct? Per Work Package and standards
2. Termination location correct both ends? Per Work Package
3. Routing / Segregation correct? 5.1
4. Cable lacing secure & correct? 5.5
5. Protection of wire? 5.4
6. All labeling correct? 8.3, 8.4
7. BNC / LCC's crimped correctly and installed per standard? 7.2
8. Bending radius correct? 5.3
9. Tested? 7.2.1
10. Other
- FIBER -
1. Type & gauge correct? Per Work Package and standards
2. Termination location correct both ends? Per Work Package
3. Terminations correctly seated at one or both ends? 7.9
4. Routing correct? 5.1
5. Protection of fiber? 5.10.4
6. Cable lacing secure & correct? 5.10
7. 12 strands or less in trough? (OFNR/P cable) 5.10.10
- 12 strands or more on fiber rack? (OFNR/P cable only) 5.10.10
8. All labeling correct? 8.3, 8.4
9. Bending radius correct? 5.10.6, 5.10.7
10. Slack limits and sotrage adhered to? 5.10.2
11. Tested? 7.9.1
12. Other
- TIMING -
1. Type & gauge correct? Per Work Package and standards
2. Termination location correct both ends? Per DWP
3. Leads correctly terminated at both ends. *Note: Shield grounds shall be terminated at ONLY one end unless specifically directed otherwise? 7.7
4. Routing correct? 5.1
5. Protection of wire? 5.4
6. Cable lacing secure & correct? 5.5
7. All labeling correct? 8.4
8. Bending radius correct? 5.3
9. Completed in maintenance window? 2.9.1
10. Tested? 2.8
11. Other
- ALARMS -
1. Type & gauge correct? Per Work Package and standards
2. Termination location correct both ends? Per Work Package
3. Routing correct? 5.1
4. Protection of wire? 5.4
5. Cable lacing secure & correct? 5.5
6. Connections correct at both ends? 7.3, 7.7
7. Bending radius correct? 5.3
8. All labeling correct? 2.7.1.1, 8.4
9. Alarm record book completed? 2.7.1.1
10. Tested with NMA? 2.7
11. Other
- POWER CABLE -
1. Type & gauge correct? Per Work Package band standards
2. Termination location correct both ends? Per Work Package
3. Terminations properly crimped and connected at both ends? 9.6
4. Routing correct? 5.1. 9.2
5. Protection of wire? 5.4
6. Bending radius correct? 5.3
7. Supported & secured correctly? 5.5, 9.2.3
8. Power/return fiber tags attached and labeled both ends? 8.11
9. H-taps crimped correctly, taped, cover applied and tied with twine? 9.6.8
10. No-ox applied on connections & fuses? 9.6.4
11. Power Cables banded together in panned rack? 9.2.3
12. Proper voltage and polarity verified and tested? 2.8
13. Completed in maintenance window? 2.9.1
14. Other
BDFB or POWERBOARD -
1. Fuse location correct? Per Work Package and standards
2. All labeling correct? 8.10
3. Completed in maintenance window? 2.9.1
4. Other
MISC. FUSE PANEL -
1. Fuse location and size correct? Per Work Package and Standards
2. Alarm Fuse Indicator Pin? 8.9.1.2
3. All labeling correct (ie - 48V, shelf label)? 8.10.5
4. Fuse Book has Shelf, Amperage and RR? 8.9
5. If service affecting, completed in maintenance window? 2.9.1
6. Other
CABLEHOLES / FIRESTOPPING -
1. Closure sealed properly? 4, 3M standards
2. Tagged and signed properly? 4.3
3. Location designated top/bottom? 4.4
4. Other
MISC. ENVIRONMENT -
1. Trash removal completed? 2.3.10
2. Bill of lading filled out? 14.2
3. Hazardous material disposal arranged? (Chapter 12)
6. Work area protection? 2.3.6
7. MOP's/Job papers removed from equipment and walls? 2.3.10
8. Foreign Object Ground tested?
If so, what was the reading _______ 1st test __________2nd test
9. Other
DOCUMENTATION -
1. Records/Drawings, installer marked shall be noted 8.18.4
* copy at site?
* copy sent to WMC?
- RED - 8.19.1
All equipment additions
All relocations
All assignment changes
Record title box changes & quantities
- YELLOW - 8.19.2
All equipment being removed from the CenturyLink facility.
If frame numbers, quantities, assignments, change, highlight old numbers
- GREEN - 8.19.3
All "record only" changes
New information regarding existing COE configurations
2. Engineer notified of any & all changes? 2.1.10
* Put note in Job Log that engineer was notified of changes and date recorded. *
3. MOP's (With start and finish time/date and all relay racks touched). Chp 15
4. JIM's - Chp 13
5. Test Record RG47-0157 - Chp 13
6. Document & Material Disposition Form RG33-0043 - Chp 13
7. Job log RG41-0046 - Chp 13
8. ICN RG47-0002 - Chp 13
9. Most recent release of Job Specification - Chp 13
10. NMA # on ICN , Job Log, and Installation assignment and Capacity sheet RG41-0170 2.7.2.1
11. NCMS # on ICN? 14.9.6, 15.9
12. Other
COLLOCATION ONLY - CHAPTER 16
1. CLEC Area
- Is the floor taped (if cageless)? Per Work Package
- Is the cage built? 16.1.4 and Per Work Package
- Is the cage grounded? 16.4.2
- Are the bays labeled? 16.3.2
2. Are CLEC Provisioning Forms required? 14.17, 16.6.1
3. Is the Material Disposition Form(s) needed? 14.3
4. Cable slack to required lengths? Per Work Package
5. CLEC CLLI code ,floor number,cable name and cable count tagged on cables and labeled on equip.? 16.3.1
6. Cable secured to rack or fence? 16.5.3
7. Lockout tagout on power source? 8.27
8. IFB Feed Terminal/NID exist? Per DWP
9. Bay Mounted Line Sharing Splitter Cards SEATED? Per W. Pkg.
10. Other
Collocation-Outward Augment (Decommission, Power Reduction, all other removal work)
1. Cables secured, coiled, or tied to rack if reusable? 16.5.3
2. Cables labeled with 2 "Collocation Spare (For Reuse) tags" 1 for each end if reusable? Estimated slack cable footages on tag? 16.5.2
3. All blocks stenciled & labeled if reusable? 8.19.6
4. Power cabling removed from source, tagged and coiled and secured near source for future reuse? 16.5.2
5. Power fuses removed and circuits breakers deactivated and stenciled as spare? 16.5.2
6. Identifying tags attached to colo area or cage (CLEC provisioning forms)? 14.17
7. Yellow or white tape with black lettering used when no place for tags? 8.19.16
8. Is CLEC equipment removed from CLEC site? (Physical) 16.5.2
9. Is CLEC site condition restored (i.e. floors, holes, A/C, stantions, etc.)? 2.3.10, 2.3.13
10. Has Virtual Equipment been removed and delivered to SICM? 16.5.1 and Per DWP
11. Has fuse position been tagged if reserved? 16.5.1
12. Cable measurements sent to engineer?
13. CLEC Name removed from all labeling? 8.19.6
14. CLEC Sheets complete (one copy in job pkg., one copy in folder hung on cables)? 16.5.1 and Per DWP
15. Other
Form Completed by: | Date: | Title:
THIS SECTION TO BE FILLED OUT BY STATE INTERCONNECT MANAGER (SICM) or CenturyLink Representative ONLY
CLEC FINAL HANDOFF
1. Verify final payment
2. Schedule handoff (SICM, ATR, RE, COM & CLEC)
3. Review access policies
4. Verify card reader
5. Designate CLEC access location
6. Reinforce cell phone policy
7. Reinforce 77350 Standards
- MOP requirement
- identify staging area/masonite policy
- grounding requirements
8. Provide keys/obtain receipt
9. Provide COM phone & pager
10. Provide emergency and maintenance phone numbers
11. Provide tech pub URL location
12. Provide CLEC Provisioning Forms
- provide all detailed data necessary
- label cable ends
13. Verify fiber jumpers have been placed for shared fiber entrance
14. Express fiber withdrawn from CO? Shared fiber unspliced in POI?
15. Obtain CLEC acceptance/completion form
16. Provide contact information for installation of AC outlets for Cageless Collocation
17. Virtual Decommission - CLEC-owned equipment returned to CLEC?
18. Other

## RG47-0162 Detailed MOP
0
Detailed
Method of Procedure
Service Assurance Contact Numbers:
800-830-0722 NROC & Alarm Center |  |  |  |  | 800-341-8188 Switch/Sw Pwr. * Note for Switch & Switch Pwr DMOPactivity use RG47-0162 (09/03 Rev.1)
800-258-8144 Net Facility Center |  |  |  |  | 800-879-1200 Network Event Management Ctr.
Service Assurance Power Contact No.: 1-800-713-3666
Start Date: |  |  |  | Start Time: |  |  |  | Completion Date: |  |  |  | Complete Time:
CenturyLink Fireworks No: |  | 0 |  |  | Supplier Order Number: | [5 empty] | System Type:
Central Office Name: |  | 0 |  |  | CLLI: |  | 0 |  |  |  | Date:
Design Engineer: |  | 0 |  |  | Installation Service Supplier: |  | 0 |  |  |  | Service Supplier Rep (Print Name): |  | 0
CenturyLink Representative Approver (Print Name): |  |  | 0 | [7 empty] | Service Supplier Rep Contact #: |  | 0
Identify equipment to be installed, modified, or removed:
Planned Network Activity Registration Number |  |  | Job Type |  |  | Power |  |  | IOF |  | Other
0
If there is not a CO Operations manager or CenturyLink representative on site (after DMOP is approved and before beginning work) and/or you suspect that you’ve caused a service interruption, call as indicated: Switch/ Switch Power/ Power: 800-341-8188 option 1. * Note for Switch & Switch Pwr DMOPactivity use RG47-0162 (09/03 Rev.1) Toll/ IOF/ Synchronization/Timing/Other: 800-258-8144
Detailed below are all the steps necessary to explain the work that is to be performed. Steps will be numbered, and appear in the order in which they will occur, with the work operation responsibility indicated by checking the appropriate boxes. Work will not begin until this form has been reviewed and signed by CenturyLink and Supplier representatives. This form may be duplicated if additional space is required. All information must comply with CenturyLink Technical Publication 77350 or applicable CenturyLink Technical Publication.
Have you Considered?
• Added or removed equipment with potential to impact service or working equipment | [5 empty] | • Hazardous materials handling and disposal |  |  |  |  | • Establishing a bridge with the NROC to monitor the office
• Eye wash, battery spill kit, First Aid available | [5 empty] | • Location of spare fuses |  |  |  |  | • Office records/drawings available and corrected
• Equipment Compatibility | [5 empty] | • Before and after tests |  |  |  |  | • Documents referenced in the MOP on-site
• Affected Working Circuits | [5 empty] | • Emergency restoration plans |  |  |  |  | • Back out procedures
• Work area protection | [5 empty] | • All applicable Product Change Notices have been reviewed/applied |  |  |  |  | • Fuse alarm operation
• Special tools/ insulated tools /materials | [5 empty] | • Cables have been metered and traced |  |  |  |  | • Personal Protection Equipment
Question Your Work
# | ITEM | [11 empty] | Date and Initial (Service Supplier)
1 | Prior to commencement of work operation(s), I have requested proper coverage. g CO Operations Representative notified? gHas everyone who needs to know about the impact of this work been notified? | [11 empty] | Yes |  | No
2 | Can I prevent or control service interruptions? | [11 empty] | Yes |  | No
3 | Is this the right time to do this work? Check proper Maintenance Window/time (M-F) Time: (Sa-M) Time: | [11 empty] | Yes |  | No
4 | I am trained and qualified to do this work? | [11 empty] | Yes |  | No
5 | Is the supporting documentation current and error-free to minimize all risks associated with this task? | [11 empty] | Yes |  | No
6 | I have everything I need to quickly restore service if something goes wrong? | [11 empty] | Yes |  | No
| w Step-by-step "backout" procedures | [11 empty] | Yes |  | No
| w Cables tagged for ease or reconnection | [11 empty] | Yes |  | No
| w Spare fuses of the proper amperage for the equipment relevant to this DMOP. | [11 empty] | Yes |  | No
| w The proper material (e.g., lugs, screws/bolts/nuts, connectors, cable/wire, etc.) | [11 empty] | Yes |  | No
7 | I am using the right tools to perform this work. | [11 empty] | Yes |  | No
8 | In the event of a service interruption, I will complete the RG47-0013 and notify:
| w CenturyLink Network Event Management Center: 800-879-1200 Option 1 | [11 empty] | Yes |  | No
| w CenturyLink Central Office Operations | [11 empty] | Yes |  | No
| w My immediate Supervisor | [11 empty] | Yes |  | No
9 | Working equipment that has been deactivated/powered down/removed from service in order to complete these procedures will be placed back in service. | [11 empty] | Yes |  | No
10 | I have identified the locations of essential and/or government circuits such as:
| w 911 | [11 empty] | Yes | No | NA
| w Federal Aviation Administration (FAA) | [11 empty] | Yes | No | NA
| w System Signaling 7 (SS7) | [11 empty] | Yes | No | NA
| I have previously submitted the PNAR and notified NROC, so that they could initiate release requests to ensure proper authorization.* | [11 empty] | Yes | No | NA
| I have ensured that these circuits have been properly identified, labeled, and that the NROC has contacted the appropriate representatives to obtain the proper work release authorization(s). | [11 empty] | Yes | No | NA
* Required for upgrades/retrofits that do not use the CIA process. The Service Supplier must initiate the PNAR at least 10 days prior to performing the upgrade/retrofit so that the NROC can obtain the releases. * IF YOU ANSWERED "NO" TO ANY OF THE ABOVE -- CALL YOUR SUPERVISOR PRIOR TO JOB START
RESPONSIBILITY
S T E P # | S U P L | Q W E S T | S S P * | DESCRIPTION OF WORK OPERATION
0 | [9 empty] | 0

## RG47-0165 Common Sys Ord Form
|  | Fax order to: | WMC AA- AZ, MT, NM, WY, NE, IA, OR Susan Agostine 303-707-7987 |  |  | Date
|  | 303-707-9673 | WMC AA CO, ND, SD, MN, WA, ID, UT Andrew Noworytta 303-707-5029
City | State | Work Type | Fireworks Proj. No. | Job No. Ref# | Job ID | ACCT Codes
0 |  |  |  | 0 | 0
Address ID | CLLI code | Engineer's Name | Engineering RC Code | Engineering Company |  | Install Comp Date
0 | 0 | 0 | 0 |  |  | 0
Installation Manager |  | Ordered By | Installer Pager | Installer Phone | Install Company | RFS Date
0 |  | 0 | 0 |  | 0
Ship to:
Special Shipping or Material Staging Instructions (shipping to CO site must be approved by Installation Supervisor or WMC Manager):
Standard shipping method is ground, all other must be approved by departmental Director.
QTY. | PART NUMBER | MANUFACTURER | CATALOG DESCRIPTION |  |  | CONSUMABLE MATERIAL ITEM Y/N
(Mandatory) | (Mandatory) | (Optional) | (Mandatory) |  |  | (Mandatory)

## RG47-0166 Missing Mat Form
JOB SITE MATERIAL INVENTORY FOR MISSING ITEMS
DATE:
FIREWORKS PROJ. NO.# | 0
JOB # | 0
OFFICE/CLLI: | 0
INSTALLATION VENDOR: |  | 0
CONTACT NAME: |  | 0
CONTACT NUMBER: |  | 0
Bill of Material Item # | Part # | Description | Quantity
Comments:

## RG47-0168 App Letter of Dev
0
Application for Letter of Deviation
(Completed by the Installation Service Supplier)
. | Issued in rare cases when all othr viable engineering options have been explored and eliminated
. | Used for one-time, site-specific conditions and is documented accordingly.
. | Not valid solely for wholesale or economic concerns.
. | Not used to remedy quality workmanship defects
. | Not to be used to continue non-standard practices that may have bee applied in the past, or
where new standards have superceded the old (i.e., earthquake bracing upgrades due to
seismic zone changes).
. | A Letter of Deviation should be approved prior to the Installation start date, but must be
approved prior to the Installation complete date.
. | All affected Central Office drawing layers must be marked accordingly.
Installation Service Provider:
Provide a detailed description of the rationale for applying for a letter of Deviation
(include: all applicable reference drawings / sketches, safety, environmental, technical,
and service concerns. Identify the exact Planning & Engineering Guidelines (PEG), technical documentation or
Technical Publication chapter, and paragraph / section the deviation applies to:
Date of Application:
State: | 0 | Central Office: | 0 | Fireworks Proj. No. | 0
Location within Central Office:
Deviation submitted to Design Engineering Representative:
Name of Application Originator:

## MRFnoshading
LEAD-ACID BATTERY RECYCLING REQUEST FORM
CONTACT PERSON |  |  | PHONE NUMBER |  | FAX NUMBER |  | LCTL, LNS, NNS or GS |  | COST CENTER |  | PICKUP RECORD NUMBER | DATE
ALTERNATIVE CONTACT PERSON |  |  | ALT PHONE NUMBER |  | T - Company Code |  | BATTERY PICKUP INFORMATION: |  |  | YES/NO | BATTERY PICKUP INFORMATION: | YES/NO
[7 empty] | ACCESSIBLE BY TRUCK? |  |  |  | LIFT GATE REQUIRED?
LOCATION OF MATERIAL: |  |  | ADDRESS |  |  |  | LOADING DOCK AVAILABLE? |  |  |  | CARRIER TO SUPPLY PALLETS?
CO. Name if Diff. Than CenturyLink | [6 empty] | FORK LIFT AVAILABLE? |  |  |  | IS THE PICK-UP SITE STAFFED?
|  |  | CITY |  | STATE, ZIP |  | PALLET JACK AVAILABLE? |  |  |  | BATTERIES LEAKING/DAMAGED?
MARK "Y OR N" IN THE APPLICABLE BOXES. THIS WILL SPEED UP THE RESPONSE TIME
SITE: SPECIAL INSTRUCTIONS
LN NO. | QTY | BATTERY DESCRIPTION | CONVENTIONAL (FLOODED) or VRLA (SEALED) | MFG | MODEL # | PALLET NO | WEIGHT PER BATTERY | WEIGHT PER PALLET | COMMENTS
1 | 0 | [6 empty] | 0
2 | 0 | [6 empty] | 0
3 | 0 | [6 empty] | 0
4 | 0 | [6 empty] | 0
5 | 0 | [6 empty] | 0
6 | 0 | [6 empty] | 0
7 | 0 | [6 empty] | 0
8 | 0 | [6 empty] | 0
9 | 0 | [6 empty] | 0
10 | 0 | [6 empty] | 0
11 | 0 | [6 empty] | 0
12 | 0 | [6 empty] | 0
13 | 0 | [6 empty] | 0
14 | 0 | [6 empty] | 0
15 | 0 | [6 empty] | 0
16 | 0 | [6 empty] | 0
| 0 | = TOTAL NUMBER OF BATTERIES | [5 empty] | 0 | = TOTAL WEIGHT OF BATTERIES
NOTE: ALL BATTERY CABLES & METAL SLEEVES MUST BE REMOVED FROM BATTERY CELLS AND ALL BATTERIES MUST BE SHRINK WRAPPED TO A PALLET PRIOR TO SHIPPING.*** DAMAGED OR LEAKING BATTERIES MUST BE KEPT SEPARATE FROM OTHER BATTERIES HELD FOR RECYCLING, AND CONTAINED SO THAT LEAKAGE INTO THE ENVIRONMENT DOES NOT OCCUR. PLEASE CHECK THE APPROPRIATE BOX IN THE BATTERY PICKUP INFORMATION SECTION AND NOTE THEIR CONDITION IN THE COMMENTS SECTION OF THIS FORM. REPORT ALL SPILLS TO YOUR REGIONAL EHS MANAGER - CALL 800-733-1250 OPT. 4. FOR EHS ASSISTANCE - OPT 6.
COMPLETED BY: |  |  |  |  | E-MAIL COMPLETED FORM TO:
tony.a.myers@centurylink.com
DATE:
For process inquiries call: AR&D at 913-390-2589
PHONE NO:
Updated May 2013
Note on L2: cam3714: Pickup # will be provided by AR&D

## REGN 154-004-001RG
0
Exhibit 1
Environmental Equipment Notification - Batteries
This form is to be completed for each battery string installation, removal, and replacement project. To ensure appropriate
permitting, agency notification, and EHS review, this form should be faxed to EHS at 303-992-7111 or may be e-mailed to
CenturyLInk EHS@qwest.com with 30 days of the estimated project date. Questions regarding this form can be directed to the EHS
Department at (303) 992-7091
SECTION A - Project Information
Facility
Name: | 0
CLLI
GEO Code: |  | 0 |  | Code: | 0
Street: | 0
City & State: |  | 0
Project
Contact: |  |  |  |  | E-mail:
Phone |  |  |  |  | Fax
Number: |  |  |  |  | Number:
SECTION B - New Batteries
The following information should be noted for each set of batteries to be installed. If more than two types of batteries are to be
installed, submit additional forms as necessary.
Battery Install 1
| Est. Install Date: |  |  | Battery Type:
| Manufacturer |  |  | Model:
| No. Strings: |  |  | Jars per string:
Location in Buildings:
Battery Install 2
| Est. Install Date: |  |  | Battery Type:
| Manufacturer |  |  | Model:
| No. Strings: |  |  | Jars per string:
Location in Buildings:
SECTION C - Removed Batteries
The following information should be noted for each set of batteries to be removed. If more than two types of batteries are to be
removed, submit additional forms as necessary.
Battery Removed 1
| Est. Removal Date: |  |  | Battery Type:
| Manufacturer |  |  | Model:
| No. Strings: |  |  | Jars per string:
Location in Buildings:
Battery Removed 2
| Est. Removal Date: |  |  | Battery Type:
| Manufacturer |  |  | Model:
| No. Strings: |  |  | Jars per string:
Location in Buildings:
TABLE A
States
FL
Global Hosting and Data Center Operations
CA, ID, MT, NV, UT, WY
CO, OK
IL, MN, ND, NE, SD, WI
GA, NC, SC, TN, VA
IA, IN, KS, MI, MO, OH
OR, WA
AZ, NM
AL, AR, LA, MS, TX
CT, DC, DE, KY, MA, MD, ME, NH, NJ, NY, PA, RI, VA, VT
Name |  | Title |  | Phone Numbers |  | Email Address
Ed Clement |  | Manager Global Hosting and Data Center Operations |  | 913-353-7290 Office 913-707-8373 Mobile |  | edward.b.clement@centurylink.com
Gerard Breen |  | Regional Environmental Manager |  | 612-798-2424 Office 612-275-8352 Mobile |  | gerard.breen@qwest.com
Bob Harding |  | Regional Environmental Manager |  | 919-562-2810 Office 919-980-0474 Mobile |  | robert.d.harding@centurylink.com
Joe Robertson |  | Regional Environmental Manager |  | 253-372-5184 Office 425-495-6804 Mobile |  | joseph.robertson@centurylink.com
Stephanie Miller |  | Regional Environmental Manager |  | 303-441-6159 Office 501-680-8141 Mobile |  | stephanie.miller@centurylink.com
Matthew Brunkow |  | Regional Environmental Manager |  | 602-630-4444 Office 602-400-8932 Mobile |  | matthew.brunkow@centurylink.com
David Burk |  | Regional Environmental Manager |  | 660-429-7155 Office 660-864-9359 Mobile |  | david.m.burk@centurylink.com
Harlan Pincus |  | Regional Environmental Manager |  | 914-686-7952 Office 914-420-2528 Mobile |  | harlan.pincus@centurylink.com
Kevin Robison |  | Regional Environmental Manager |  | 801-237-3006 Office 801-598-3020 Mobile |  | kevin.robison@centurylink.com
Clarence Watson |  | Environmental Project Manager |  | 501-241-6351 Office 318-282-7230 Mobile |  | clarence.watson@centurylink.com
Jennifer Scarpino |  | Regional Environmental Director |  | 407-889-1531 Office 321-289-2720 Mobile |  | jennifer.scarpino@centurylink.com

## Form 820 Gen Tst Chklst
GENERIC TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  | YES | NO
Equipment Verification
Frames located per floor plan
Installed per drawings
Equipment is what was ordered
Equipment options are correct
Spare equipment provided per ordering spec (if applicable)
Power feed to equipment checked
Workmanship
Frame alignment and equipment mounting
Relay rack numbering
Wiring and cabling
Equipment numbering and lettering
Cable openings sealed
Cable racks and other ironwork
Power and fusing (spare fuses available also)
Performance Tests
Tests per recommended equipment manual
Tests per Test & Acceptance package sent out with job (contact the Engineer if no such package sent)
Documentation
"As-built" drawings sent back to engineering
Replacement drawings
Initial battery charge reports (if applicable)
Equipment manuals received
Original test results retained
Alarms
Affected alarms tested prior to work start
Local and audible alarms (as applicable) tested prior to work start
Remote alarms installed and tested with NROC Alarm Center (1-800-713-3666)
Name of NROC Center Contact with whom alarms were tested:
Other
Comments (all No answers must be commented on)

## Form 821A Pwr Rm Lhtg chklst
POWER ROOM LIGHTING TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  | YES | NO
1. Lighting provided in the power areas is adequate, and located in accordance with the SITE: record lighting plan drawing
2, As a minimum, emergency and task/stumble lighting is available in stairwells, over the "power board", over the engine control panel and AC transfer switch, over the AC switchgear, and in the engine room
3. Emergency and task/stumble lighting works
4. Feeding fuse/breaker positions and emergency and task/stumble lighting fixtures are properly stenciled as to the equipment they feed or where they are fed from
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## Form 821B Alm Tst Chklst
ALARM AND/OR POWER MONITOR/CONTROLLER (PSMC)
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Associated Power Plant: |  | ANCR#:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  |  | YES | NO
1. Complete copy of suppliers' manuals and drawings available on site
2. Verify accuracy of the database, and ensure an electronic backup is made where applicable
3. Verify that analog channel readings are within 1% of the values measured by plant meters or by technician's hand-held meter
4. Bring in each binary alarm associated with this monitor (or other alarming device) and verify that technicians in Power NROC (800-713-3666) receive the alarm over NMA
A. There is local indication of the alarm on the monitor, if monitor is capable of this function
B. If monitor is capable and equipped, verify the difference between Minor Rectifier Fail (1 rectifier), and Major Rectifier Fail (2 or more rectifiers failed)
5. Bring in binary alarms associated with the threshold settings of analog points (e.g., low voltage, etc.), and ensure that these alarms report locally on monitor and over NMA
A. Analog points' binary thresholds are set properly (according to REGN 154-103-001)
6. If monitor is controlling High Voltage Shutdown (HVSD) verify proper operation
7. Ensure that all binary, analog, & control points requested on engineering job were provided, & ensure that there is a record left in office on paper and/or on disk of the assignments
8. If monitor is capable and equipped, verify the difference between Minor Converter Fail (1 converter), and Major Converter Fail (2 or more converters failed)
9. Verify security levels (e.g., different passwords), and dial-back numbers (if applicable)
10. System reboots properly after being turned off/on
11. Verify through NROC Center or NMA database group continuity of X.25 link where applicable
12. When monitor is equipped with control functions, verify proper operation of these functions (e.g., rectifier shutdown/restart, engine start/stop, etc.)
13. Verify that laptop can communicate with monitor over RS-232 port
14. Verify communication with unit over a dial-up
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: Use supplier, Telcordia, and CenturyLink documentation as a guide to performing the tasks above. NOTE: When testing alarms and functions, be sure not to interrupt service unless done during the Maintenance Window and with notification to appropriate personnel
Comments (all No answers must be commented on)

## Form 821C BDFB PBD Chklst
BDFB, POWER BOARD, OR FUSE PANEL
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  | YES | NO
1. Proper equipment was ordered and is sized appropriately for the application
2. Verify proper load bus arrangements
3. Verify proper return bus options
4. Verify accuracy & proper operation of the digital or analog meters & current shunts
5. Test fuse alarms for proper operation and continuity to NROC (Note: BDFBs and other secondary fuse panels are not monitored by the Power NROC group, but by the groups who monitor the equipment served by these secondary protection devices)
6. Verify proper placement, anchoring, and stenciling of the bay(s) and/or shelves
7. Ensure that all fuse/breaker assignments are properly marked/stenciled for the loads they feed, and that all incoming and outgoing cables are properly tagged
8. Verify proper connections of wires/cables to the fuse distribution, ground, and battery return busses/connections
9. Verify proper cable routing
10. Verify proper frame and central office grounding
11. Ensure that BDFBs are equipped with a sticker(s) specifying the maximum feeder load (50% of the protector size) for each feeder
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: Use supplier documentation as a guide to performing the tasks above. NOTE: Work on a Power Board or BDBF has the potential to interrupt service. Service shall not be interrupted when installing primary or secondary distribution panels. Cutover of a BDFB or Power Board should probably occur during the Maintenance Window if the power plant is already up and supporting loads.
Comments (all No answers must be commented on — use the back of this form if necessary)

## Form 822 Battery Tst chklst
BATTERIES & BATTERY STANDS TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Associated Power Plant: |  | Battery String #:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  | YES | NO
1. Battery stands and batteries are stenciled or identified with a minimum of installation and/or manufacturing date (on batteries), string numbers/letters, and cell numbers.
2. Batteries and connectors are free of the following defects.
A. Cases crazed, cracked, bulged, corroded, or leaking
B. Level indicators stuck or missing
C. Cover or post rise, and/or post corrosion
D. Excessive positive plate growth or strap growth
E. Excessive plate bowing or cracking
F. Excessive needle growth
G. Lead-sulfate crystals (this should be checked after batteries have received their full initial charge)
3. Electrolyte level is proper, and limits for electrolyte level are marked on the batteries.
4. Proper vent and filler caps or funnels are installed, and flame arrestors are equipped with dust covers.
5. Battery records/logs and any manufacturer documentation are on-site and easily accessible. The Storage Battery report (RG47-0001) should have been filled out by the installation vendor.
6. Neutralizing agents and protective equipment are available nearby for use as required in the battery area (eyewash, baking soda or equivalent, rubber gloves, goggles, rubber apron).
7. Thermometers, hydrometers, and holders are furnished and mounted as required.
8. Check batteries and intercell connections integrity by placing string on a short 5 minute discharge test into a real load or load box load. (This requirement is optional due to the fact that some battery strings are installed long before they are connected to the real load.) As a minimum attempt to determine if connections were properly tightened with a torque wrench.
9. All voltage readings are within (+-) 0.05 of the float average (e.g., 2.20 V/cell)
10. Spill and disposal procedures are posted near the batteries.
11. Battery stand is braced appropriately for earthquake zone in which site is located.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix.
Comments (all No answers must be commented on)

## Form 823A Rect Tst Chklst
RECTIFIER TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Rectifier #’s |  | Associated Power Plant
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM: |  |  | YES | NO
1. Rectifiers are properly assembled, installed, and stenciled or identified
2. Correct type & capacity fuses are provided, & all fuses are clean & properly installed
3. AC power connections are properly made. Ensure proper transformer taps and phase rotation where applicable
4. Ensure that correct rectifier (size, type, AC input, etc.) was ordered, including correct wiring or apparatus options
5. Rectifiers operate per individual operation tests, and basic operational features work
6. Plant meters are accurate and properly adjusted
7. Alarm settings are adjusted to requirements, and proper alarm signals are transmitted (ensure alarms reach the NROC Center)
8. Current limiting and partial load features of units are set and adjusted properly
9. High voltage shutdown (HVSD) feature operates properly, and all other DIP switches, potentiometers, and other options are properly set, including alarm thresholds
10. Outputs of all units are stable (non-hunting, except for load sharing variations), & rectifier float voltages are properly set for battery type (see REGN 154-103-001) & load sharing
11. Test rectifier fail alarms for continuity to the NROC Center
12. Simulate an AC power failure to verify that the units' auto-restart capability and current walk-in feature operate properly when AC power is restored. Ensure also that alarms clear and that the units return to float voltage
13. All rectifiers are capable of operating, regulating, and current limiting at full load
14. Ensure AC fuse panel(s) feeding rectifiers have adequate spare capacity. If not, notify Real Estate
15. For multi-phase fed rectifiers, verify appropriate operation or shutdown during phase failure
16. Ensure proper selection and routing of rectifier control cables to plant controller
17. Ensure rectifier frames are properly grounded & that battery return cables are properly grounded & sized, dependent on whether plant is integrated, isolated, or combined
18. Ensure rectifier DC output cables are properly installed, & sized according to Tech Pub 77385 (for 200 and 400 Amp rectifiers), or manufacturers’ recommendations (all other sizes)
19. Ensure that there is adequate ventilation & heat dissipation so rectifier will not overheat

## Form 823B Pwr-Batt Tst Chklst
POWER/BATTERY PLANT TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Power Plant: |  | Location:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. All battery distribution cables are of correct size and type, and properly terminated
2. All equipment of control and distribution bays are correctly stenciled or identified
3. All control circuit, charge, and discharge fuses and/or circuit breakers are of the correct type and 4. capacity, and located as shown on the drawings
4. Alarm fuse positions are equipped with correct fuses, and fuse and circuit breakers are properly designated as to the equipment they serve
5. Verify alarm operation, both locally, and to the NROC Center
6. All DC meters are calibrated and properly adjusted
7. All fuses are tight in their respective fuse holders, and fuses and circuit breakers are free of excessive heat
8. The battery float voltage is correct (check after meter calibration, and initial charging of the batteries)
9. The voltage alarm settings are correct per REGN 154-103-001
10. Spare fuses are provided, and properly located and designated, on or near the battery plant
11. If LVD is used (use only where required, such as with a DMS®10 switch), ensure setting is -43.25 V or less.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## Form 824A Cnvt Plnt tst chklst
CONVERTER PLANT TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Associated Power Plant: |  | Location:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. The converter plant is properly assembled and installed (including properly made electrical connections, and stenciled or identified
2. The input and output fuses are the correct type and capacity
3. The discharge fuse alarms are operative, and connected properly, and spare fuses are available
4. The voltage alarm levels are properly adjusted to specified limits
5. All alarms function properly, and are received by the NROC Center
6. High voltage shutdown (HVSD) feature operates properly
7. The converter plant meters are accurate, and properly adjusted, and all other LEDs or other indicators work properly
8. The output voltage is adjusted within the specified limits, and can be accurately read from the test jacks
9. The output current limit is properly set, as well as any other options set through DIP switches or potentiometers
10. Verify that the converter plant functions properly under load for at least 30 minutes, and that there are no problems if the converters are switched on and off.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: When testing alarms and functions, be sure not to interrupt service unless done during off hours and with notification to appropriate personnel
Comments (all No answers must be commented on)

## Form 824B Res Ring Plnt Chklst
RESIDUAL RING PLANT TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Associated Power Plant: |  | Location:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. The ringing plant is properly assembled, installed, and stenciled or identified
2. Ringing plant fusing is in agreement with site drawings
3. All alarms operate properly, including transfer alarms (ensure alarms reach NROC center)
4. The transfer feature operates automatically when a power failure occurs (for units when Ring Generator 1 is AC powered), or if Ring Generator 1 fails. (This transfer also applies to those sites equipped with interruptors besides the ring generators)
5. If equipped, the transfer feature operates properly by manual or test transfer methods
6. All voltages, tone levels, and frequencies are within specified limits
7. If meters are provided, they are accurate, and within adjustments
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## For 825A Inverter Tst Chklst
INVERTER TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Associated Power Plant: |  | Location:
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. The inverter plant is properly assembled and installed (including proper electrical connections), and stenciled or identified
2. Input, output, and alarm fuses are the correct type and capacity, and output distribution is properly sized and connected
3. Simulate an AC power failure. Ensure proper operation and transfer. During outage check output voltage and frequency
4. Verify that plant is capable of operation at full load, in both AC input or DC input modes. (Use a dummy load — e.g., load box — if necessary to fully load the plant)
5. Verify proper operation of maintenance bypass, if equipped
6. Verify proper operation of transfer switch
7. Alarms operate and clear properly (ensure alarms remote to the NROC Center)
8. Verify proper operation of any automatic shutdowns (e.g., low voltage, emerg. stop, etc.)
9. Verify proper operation of all controls and indicators (meters, LEDs, etc.)
10. Ensure that the green wire ground is properly connected
11. Ensure there is adequate room and ventilation around the inverter
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: When testing alarms and functions, be sure not to interrupt service unless done during off hours and with notification to appropriate personnel
Comments (all No answers must be commented on)

## Form 825B UPS Tst Chklst
UPS TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. The UPS is properly assembled, installed, and stenciled or identified in accordance with Engineering instructions
2. The correct type and capacity fuses are provided, and all fuses are clean and properly installed
3. AC/DC power connections are made in accordance with Engineering instructions, and in compliance with Qwest CenturyLink 4. 4. Technical Publication 77355
4. Transformer taps are set properly
5. Ensure proper AC phase rotation on the output
6. Plant meters are accurate and properly adjusted
7. Alarm settings are adjusted to requirements, and proper alarm signals are transmitted. Ensure that alarms reach NROC Center
8. Correct wiring or apparatus options provided
9. Current limiting and partial load features of units are set and adjusted per Engineering requirements
10. High voltage shutdown feature operates properly
11. Outputs are stable (non-hunting, except for load sharing variations)
12. Simulate AC power failure to verify unit's auto-switch capability, and that it operates properly when AC power is restored (ensure that alarms clear when AC is restored). Check for proper return to battery float voltage
13. UPS capable of operating at full load
14. Battery chargers are operating at the required output voltage
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
NOTE: Use supplier documentation as a guide to performing the tasks above.
NOTE: When testing alarms and functions, be sure not to interrupt service unless done during off hours and with notification to appropriate personnel
Comments (all No answers must be commented on)
reference Routines EE550 and EE551

## Form 826A Eng Tst Chklst
STANDBY ENGINE TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Engine-alternators & associated equipment are located according to the floor plan drawings, & are installed according to Engineering request, & are properly sized (e.g., fuel and exhaust system piping & tubing)
2. Engine start batteries and chargers are in good condition, and installed and operating properly
3. Verify start batteries and charger per Forms 822, 823A, manufacturers’ documentation, and TPP below
4. A remote emergency stop switch/button is located outside but near the engine room, & is properly identified
5. Test records, logs, and manufacturer documentation is on site and accessible
6. Before operation, inspect for the obvious, like assembly; fuel or oil leaks; or loose, missing or damaged parts
7. Fuel in main and day tanks is sufficient and free of excess water and other contaminants
8. Oil and coolant levels are sufficient, fluids are contaminant-free, and jacket water heater is operational
9. Engine-alternator operating instructions are posted near the engine, and are clear and easy to use
10. Adequate ear and eye protection is available in the engine room, and adequate warning labels are posted
11. Ensure that engine, engine room metallic parts & lines, and alternator neutral are all grounded per Pub 77355
12. Engine crankcase breather is vented to atmosphere or discharge damper
13. With the engine mfg & the installer present perform a first test of the genset with the engine on a full load bank for 2-4 hrs (preferably run this test on site; however, the test may be done at the mfg’s location with Qwest present to observe). Observe all functions, readings, alarms, etc., & note abnormalities, paying special attention to the following:
A. Water, fuel, and oil temperatures and pressures are within limits
B. Ensure proper operation of the transfer switch
C. Frequency, current, kW, and voltage readings are correct, and within limits
D. Test all alarms during run, both locally and remotely (to Power NROC) for proper operation
E. If provided, rectifier sequencing functions properly
F. Exhaust press. < limits; no exhaust leaks; internal exhaust pipes insulated; 9" min. exhaust clear from combustibles; hot "reachable" parts guarded and/or labeled; exhaust couplings use bolted flanges with gaskets or threaded pipe; has a flex connection to engine & flex supports to allow for expansion/contraction; & end of exhaust stack protected
G. Ensure proper operation of all fuel pumps, and the day tank (where applicable)
H. Intake/exhaust fans/louvers operate (& held open by spring on AC loss), & properly sized per dwgs. (Check proper intake size by seeing if engine room door opens easily). Air intake filters properly installed? (Exhaust fans to be controlled by room thermostat, if separate.) Exhaust positioned so its gasses & heat are not part of intake air.
I. If provided, paralleling functions properly
J. Current load is reasonably balanced between phases
K. All required gauges, meters, and local and remote alarms are present as per Pub 77385
L. Test emergency shutdown
14. Check fluids and fuels after run, and visually inspect for leaks, loose parts, etc.
NOTE: Use supplier documentation, as well as TPP T.AMC.POWR.96.0008 for more complete engine Test and Acceptance
NOTE: When testing alarms and functions, be sure not to interrupt service
Comments (all No answers must be commented on — (Please use the back of this form for comments)

## Form 826B Trans Swt & AC Cklst
TRANSFER SWITCH AND AC SERVICE ENTRANCE
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Ensure proper operation of the transfer switch. Simulate an AC failure and return of Commercial AC. Ensure that all timers function properly.
2. If provided, paralleling functions properly and that there are sequencer lights or meters which properly operate if paralleling is to be done manually.
3. Ensure that drawings for the transfer switch are on site.
4. Ensure that a single line-drawing is on site (it may be physically etched or drawn on the AC switchgear)
5. Visually inspect (or thermally with a thermal gun or camera) all connections in the transfer switch and AC service entrance cabinets for tightness.
6. Ensure that the AC loads of the site do not exceed buss bar and breaker capacities in the AC switchgear.
7. Ensure that electrical safety equipment is available for the site: electrical gloves, goggles, and tags/locks for use in lockout/tagout procedures when AC work is being done and possibly fire-retardant Nomex gear.
8. Ensure that AC service entrance has a lightning arrestor and/or surge suppressor properly installed.
9. Ensure that the AC fail is monitored per phase, and that an AC fail alarm properly reports through the alarm systems to the NROC.
10. If the site is equipped with a power monitor (PSMC), verify that AC voltage (per phase, line-neutral) and currents (per phase) are monitored and reading properly.
11. Ensure that the power company transformer is adequately sized to handle the site load.
12. Ensure that the AC Service Entrance and Transfer Switch have proper grounding connections per Pub 77355.
13. Ensure that there is proper interrupt current rating coordination from the power company transformer down to the PDSCs (e.g., ensure that the K.A.I.C of the service entrance equals or exceeds that of the power company transformer, etc.)
NOTE: Use supplier documentation, as well as TPP T.AMC.POWR.96.0008 for a more complete Test and Acceptance
NOTE: When testing alarms and functions, be sure not to interrupt service
Comments (all No answers must be commented on — Please use the back of this form for additional comments)

## Form 826C Fuel Tst Chklst
FUEL TANK, FUEL SYSTEM, AND FUEL MONITOR
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Fuel in main and day tanks is sufficient and free of excess water and other contaminants
2. Ensure that outdoor tanks are placed in such a position that water will not flow into or pool on top of them.
3. If the outdoor Diesel fuel tank is aboveground in a climate where temperatures may get below 32˚ F, ensure that the tank is either using #1 Diesel fuel, or is equipped with a tank heater.
4. Visually ensure that all fuel tanks (both main and day) have containment that will contain all of the fuel in the tank in case of a leak.
5. Inspect tank(s) and all fuel piping and pumps for any leaks.
6.Ensure fuel lines are connected to engine through a flexible section.
7. Fuel Lines are installed and routed in accordance with the vendor-supplied Engineering specs and drawings.
8. Verify that an anti-siphon valve is installed on the fuel suction line at the first entrance point to the generator room. The melt link should be 195 degrees.
9. Verify that an electric fuel solenoid (operating from the engine start and/or control batteries at 12 V or 24 VDC) is installed on the supply line at each generator’s fuel pump’s flex hoses. The solenoid must be connected to the generator run circuit in the control panel.
10. Verify that fuel lines running on the floor are routed so as not to create a safety hazard. (Fuel lines lying on the floor should be covered with a metal shroud, and the shroud should be painted yellow or yellow with black diagonal stripes.)
11. Verify that the fuel lines are Aero-quip or Strotoflex hose or black iron. (Aero-quip and Stratoflex lines are permitted, but must be run inside a containment conduit. Galvanized pipes and fittings are not permitted.)
12. Verify that the fuel return line is free from all obstructions. (No gates, valves, or traps are permitted.)
13. Ensure proper operation of all fuel pumps, plus any day tank valves.
14. Ensure that a low fuel alarm is reported as a minimum (may be reported as a generic fuel system trouble) all the way to the NROC. The low fuel alarm should report when there is 8 hours or more of fuel left.
15. If site is equipped with a fuel tank monitor, ensure that it has at least a generic fuel system trouble alarm wired and reporting all the way to the NROC.
16. Ensure fuel tank monitor is equipped with a dialup modem and a working phone line (some radio sites and other sites where phone service is inaccessible may be exempt from this requirement), and that Power NROC and the local Power Crew have that number.
17. Ensure that the fuel tank monitor is equipped with paper tape and ink, and a method of storing the paper tape.
18. Ensure that all fuel lines and tanks are properly grounded in accordance with CenturyLink Tech Pub 77355.
NOTE: Use supplier documentation, as well as TPP T.AMC.POWR.96.0008 for a more complete Test and Acceptance
NOTE: When testing alarms and functions, be sure not to interrupt service
Comments (all No answers must be commented on — Please use the back of this form for comments)

## Form 827 OSP Tst Chklst
OUTSIDE PLANT SITE TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Ensure that internal and external grounding is per CenturyLink Technical Publication 77355. Ensure proper grounding of the site using a megger.
2. Do ventilation and exhaust openings have free access
3. Ensure that the site and all of the bays and wiring in the RT are properly tagged/stenciled
4. Ensure proper operation of A/C, sump pump, gas monitor and other environmental systems with the vendor present for CEVs, CECs, and huts, as applicable
5. Ensure safety equipment (e.g., fire extinguisher, first aid kit, gloves, eyewash fluid, etc.) is present, as applicable
6. Ensure that all holes in a CEV are properly sealed
7. Emergency lighting, gas monitors, environmental controllers, or any other device that should be powered by -48 VDC is connected to the DC Plant.
8. Site properly constructed, landscaped, and backfilled; and weeds are abated
9. Emergency engine connection available and sized properly. Verify that a generator can be parked within 10 ft of the transfer switch, and that the soil is such that there is access under adverse weather conditions. After turn-up, transfer the site to generator to confirm backup.
10. Site has records/forms for proactive maintenance of the power plant. Ensure that the power plant was turned up correctly per Forms 823A and B. Load tests the plant and batteries.
11. Ensure continuity of power and environmental alarms, and any other alarms to the NROC Center (Power Major, Power Minor, Intrusion, High Temperature, and Explosive Gas Alarm for CEV/Cs are a minimum). If a mux is used, verify that it is configured for phase 2 and provisioned for X.25/TL1. (See Standard Configuration and REGN 154-103-001 for power and environmental alarm standards.)
12. Lightning/surge arrestor installed in power pedestal, and power pedestal wired per the NEC
13. Confirm that controlled environment sites are set to operate within 55-85° F.
This Test & Acceptance checklist should be performed with the installer(s)/contractor(s) on site. Note on attachment all problems they fix
Comment below or attach comments (all No answers must be commented on)

## Form 828A CO Grnd Tst Cklst
CO GROUNDING TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1.The site ground is the proper size, and installed in accordance with the site record drawings, Engineering instructions, and CenturyLink Technical Publication 77355
2. Both ends of all site ground cables are tagged, and designated to show opposite end terminating location.
3. All site ground cables between floors and through wall are run through nonmetallic sleeves or conduit. If site ground leads are run through metallic conduit or sleeves, both ends of the conduit or sleeve are bonded to the site ground lead.
4. Isolated frames, cabinets, rectifiers, etc. containing AC service are properly grounded (usually identified with green-wire ground).
5. If associated switching system uses isolated grounding, integrity must meet the system requirements spelled out in Qwest CenturyLink Technical Publication 77355.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix.
For a complete grounding review, contact the NROC.
Comments (all No answers must be commented on)

## Form 828B Pwr Bar & Cable cklst
POWER DISTRIBUTION BUS BAR & CABLING
TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Associated Power Plant |  | Location
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. AC bus duct and conduit is installed in accordance with site record drawing layout, and the manufacturers' specifications.
2. The proper type and size fuses and/or circuit breakers are installed in AC bus duct plug-in units
3. Warning labels are placed at all access openings and end sections of AC bus duct, as required.
4. Bus bar is installed in accordance with site record drawing layout
5. Bus bars and risers are stenciled to properly identify CHARGE, DISCHARGE, BAT, GRD, voltage, etc.
6. The ammeter shunt is properly mounted and stamped to indicate voltage and ampere rating.
7. Installation meets CenturyLink workmanship standards, and is in accordance with Engineering standards and drawings, as spelled out in CenturyLink Technical Publications 77350, 77351, 77352, 77355 and 77385
8. Bus bars, joints, and terminating connections to bus bars are free of excessive heat. (Technicians may use heat strips, or heat guns to determine heating. If major problems are suspected, a Power NROC Tech Support person may be called in to do a scan with a thermal camera).
9. Power cable is routed in accordance with site record drawings.
10. Power cable is run and secured on cable racks.
11. Adequate insulating protection is provided on cable rack straps, stringers, thread rods, auxiliary frame bars, and other metallic objects where power cable makes contact with sharp surfaces.
12. Power cable insulation is free of damage.
13. Terminating wires and cables are properly tagged and designated at both ends of conductors when required.
14. All cables listed on power cable running list are installed with correct type and size of cable as specified, or otherwise calculated.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## Form 829A Pwr Flr Plan Cklst
POWER AREA FLOOR PLAN TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Associated Power Plant |  | Location
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. Power equipment is located and designated as shown on floor plan drawing.
2. All cable holes appear to be closed properly (wall, ceiling, and floor type, as applicable).
3. Wall and column mounted equipment are properly located and shown on floor plan, cable rack plan, or other associated site record drawings.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix.
Comments (all No answers must be commented on)

## Form 829B Pwr Tst Chklst
POWER DOCUMENTATION TEST & ACCEPTANCE CHECKLIST
Site: | 0 | Fireworks Project No.: | 0
Associated Power Plant |  | Location
Engineer: | 0 | Job Vendor:
Date of Installation completion: |  | Date of Vendor Departure:
Tested by: |  | Date:
ITEM |  |  | YES | NO
1. All new power equipment drawings furnished on this project are in acceptable condition.
2. All power drawings that were supposed to be provided with this job were provided.
3. All operating and maintenance instructions for new or added power equipment are available and accessible at the site.
4. All installer job completion reports are available.
5. Installer(s) followed written MOPs.
Test & Acceptance should be performed with the installer on site. Note below all problems they fix
Comments (all No answers must be commented on)

## Form 840 CO Pwr Equip Inv
0
0
CENTRAL OFFICE POWER EQUIPMENT INVENTORY
OFFICE: | 0 | CLLI: | 0 | DATE:
ADDRESS: | 0 | TECH: |  | PHONE:
BATTERY PLANTS
| Plant #1 | Plant #2 |  | Plant #3
Voltage & Polarity:
Plant/Controller Mfr. & Model:
Plant Size (shunt & bus bar ampacities):
Rectifier Fr & Model:
Battery Strings & A-hr Size:
Battery Fr & Model:
Battery Installation Date:
Plant Load in Amps:
PDSC Bus Ampacity & Fdr Fuse/Brkr Size:
add Rect. max loads for total max on PDSC:
CONVERTER PLANTS
| Plant #1 | Plant #2 |  | Plant #3
Voltage & Polarity:
Fr & Model:
Associated Battery Plant:
Qty & Sizes of Converters:
Plant Load in Amps:
RING PLANT(S) |  | PSMC MONITOR and OTHER ALARM DEVICES
Fr: | Model: | PSMC Fr & Model:
Ringers: | Interrupters: | Software Version:
Tone Generators: | Installation Date: | Dial-Up #:
INVERTER(S)/UPS |  | X.25 Ckt #:
Fr & Model: |  | Other Alarm Devices (e.g., Dantel, etc.):
Size, AC Voltage/Phase: |  | ENGINE & TANK DATA
Load (AC Amp/kVA): |  | Fr & Model:
Associated Battery Plant: |  | Voltage & kW:
Installation Date: |  | Install Date (note if not Autostart):
COMMERCIAL AC |  | Fuel Type & Consumption (gal/hr):
Voltage & Phase: |  | Actual Engine Load (in kW):
Size (Amps): |  | Alitiude
Lightning Arrest Fr & Model: |  | Start Batt Fr & Model:
PORTABLE GENSET INFORMATION |  | Start Batt Install Date:
Plug Fr, Mod, & Size (Amps): |  | Xfr Switch Type/Size:
Portable Fr, Size, Fuel: |  | Day Tank Capacity (gal):
Storage Location: |  | Main Tank Type & Capacity (gal):
Tank Monitor Fr & Model:
NOTES & COMMENTS (use back of sheet as needed) |  | Tank Monitor Dialup:
Retain a copy of this form and send a copy to the Power Engineers (http://saw3/NROC/Power/power-mop/Directory.html)

## Form 841 BDFB-PBD Assign Rec
0
0
BDFB OR POWER BOARD PANEL FUSE/BREAKER ASSIGNMENT RECORD
Site: | 0 | CLLI: | 0 |  | Date:
Address: | 0
Tech: |  |  |  | Phone/Pager:
PBD/RR of this BDFB/PBD: |  |  |  |  | PANEL(s):
Fdr Fuse/Brkr PBD & Position: |  |  | Fdr Fuse/Brkr Size: |  |  | Panel Load:
Position # | Equipment & Relay Rack Fed |  |  | Fuse or Brkr Size | Mfg L-2 Drain | Mfg L-1 Drain | Actual Load
Totals
additional panels may be placed on additional sheets
List 2 drains are peak drains (fuses sized at 125% minimum of this; and cable sized from them too), and List 1 drains are average drains
assigning fuses from the bottom to the top of a bay or panel (or inside to outside for horizontal panels)
eases future installation and reduces cable congestion
as needed, contact your Design Engineer for a fuse assignment (if those are tracked in your area)
Please note if this Panel is "bussed" or "cabled" in the rear to adjacent panels (e.g., C, A2, etc.)
information for all columns may not be available to you — some columns are for Engineering use, and some for the "field"
Notes:

## Form 844 Critical Pwr Alm cklst
0
0
CRITICAL CO POWER AND ENVIRONMENTAL ALARM VERIFICATION
Alarm |  | NMA tkt # | Notes
Critical Power Alarms
Commercial AC Fail
Power Major
Power Distribution Fuse/Breaker Major
Low Voltage and/or Battery on Discharge
Very Low Voltage (if applicable)
High Voltage
Rectifier Fail Major
Ring Plant Major
Low Voltage Disconnect (where applicable)
Engine Run
Engine Fail/Major
Critical Environmental Alarms
High Temperature (of the site or any room therein)
Fire Alarm
Fire System Trouble
High Water/Sump (in cable vault, if applicable)
Open Door/Intrusion
Alarm Center Contact Person: |  |  | Alarm Center Phone:
Site CLLI: | 0 | Site Address: | 0
Alarm Telemetry System Type:
X.25 (PSMC) | e-tel (Dantel, E2A, Westronics) |  | Switch or other
NROC Tech with whom Test performed: |  |  | Phone:
It may not be wise to test some alarms except in the Maintenance Window due to the possibility to cause an outage if they are truly tested; and/or in some cases, it may be best to simply verify alarm continuity by shorting the alarm pins instead of actually bringing in the alarm, for the same reasons
Environmental Alarms may be tested by Real Estate
Additional Notes:

## From 845 OSP Equip Inv
0
0
OUTSIDE PLANT POWER EQUIPMENT INVENTORY
Common Name of Location | 0
State | 0
CLLI | 0
Address | 0
Upstream Office (serving Wire Center)
Access & Directions
Map coordinates (if applicable)
Customer (primarily for Customer Prem sites)
Site Type (RT, CEV, UE, CEC, hut, rptr, CPE)
(list RTs by type: e.g., 80 cabinet, etc.)
Date of this review
Reviewer name & contact #
Air-conditioning type & maintenance contact
Power plant type (also list J-spec, KS-, or model #)
Load (in Amps)
# Rectifiers
Rectifier type [also list the model number(s)]
Rectifier size(s)
Float Voltage
# Battery strings
Battery type (model #, KS-spec, etc.)
Battery size (A-hrs)
# cells per string
Battery installation date(s)
Residual Ring plant type (model number, etc.)
Comm. AC voltage, phase, and Amp rating
Generator Plug Mfg., type, and size
Alarm system (E-tel, X.25, overhead, etc.)
Alarm Center & Center phone #
CIRCLE ALARMS THAT ARE PRESENT (Add any others not listed here)
POWER MJ POWER MN RECT. FAIL OPEN DOOR LOW TEMP HIGH TEMP
AC PWR FAIL SMOKE/FIRE HUMIDITY SUMP PUMP COMBUSTIBLE GAS TOXIC GAS
Notes:

## Form 846 Equip Enc Alm Ver
0
0
OSP EQUIPMENT ENCLOSURE HOUSEKEEPING ALARM VERIFICATION
Alarm |  | Works? | Doesn’t Work? | N/A
Commercial AC Fail
Power Major
Power Minor
High Battery Temperature
Power Distribution Fuse/Breaker
Low Voltage and/or Battery on Discharge
Very Low Voltage
High Voltage
Rectifier Fail (list the number of these alarms if more than 1)
Ring Plant Major
Ring Plant Minor
High Temperature (of the enclosure)
Explosive Gas Alarm
Toxic Gas Alarm
Toxic/Explosive Gas Alarm (combined)
Fire Alarm
Fire System Trouble
High Water
Sump Pump Failure
Open Door/Intrusion
Ventilation/Fan Fail
Air-Conditioner Failure
High Humidity
Tech Performing Test: |  | Phone/Pager:
Site CLLI: | 0 | Site Address: | 0
Alarm Telemetry System Type:
X.25 overhead (fiber mux) | e-tel (Dantel, E2A, Westronics) |  | other (list)
NROC Tech with whom Test performed: |  |  | Phone:
Additional Notes:

## Labeling Checklist
Fill in the Shaded boxes on this worksheet. This data will then auto populate the EMG Completion Checklist worksheet. | [15 empty] | PBD | X.25 | U | CNTL
| Installed Equipment | [14 empty] | BDFB | CO-LAN | L | RMT
| Bay 1 |  |  |  | Bay 2 |  |  |  |  | Bay 3 |  |  |  | Bay 4 |  | BDCBB | NNET |  | EXPN
| RR/Cab RR: |  |  |  | RR/Cab RR: |  |  |  |  | RR/Cab RR: |  |  |  | RR/Cab RR: |  | RING
| Fiber Shelves |  |  |  | Fiber Shelves |  |  |  |  | Fiber Shelves |  |  |  | Fiber Shelves |  | -130V
| Equip. Shelves |  |  |  | Equip. Shelves |  |  |  |  | Equip. Shelves |  |  |  | Equip. Shelves |  | +130V
| Fuse Panel (s) |  |  |  | Fuse Panel (s) |  |  |  |  | Fuse Panel (s) |  |  |  | Fuse Panel (s) |  | Battery String
| DS 0 SH (s): |  |  |  | DS 0 SH (s): |  |  |  |  | DS 0 SH (s): |  |  |  | DS 0 SH (s):
| DS 1 SH (s): |  |  |  | DS 1 SH (s): |  |  |  |  | DS 1 SH (s): |  |  |  | DS 1 SH (s):
| DS 3 SH (s): |  |  |  | DS 3 SH (s): |  |  |  |  | DS 3 SH (s): |  |  |  | DS 3 SH (s):
| FMT SH (s): |  |  |  | FMT SH (s): |  |  |  |  | FMT SH (s): |  |  |  | FMT SH (s):
| Fan Shelf (s): |  |  |  | Fan Shelf (s): |  |  |  |  | Fan Shelf (s): |  |  |  | Fan Shelf (s):
If there was more equipment installed on this job than can fit in the shaded boxes, place that information in the following box and it will be added in the Equipment Added box on the EMG completion checklist form.
| POWER | [9 empty] | DS-0 |  | Frame:
| Power Bay Type | Bay Number |  | Load or Battery String |  | Fuse Panel | Fuse Position |  | Amp |  | Blocks (Horz):
Blocks (Vert):
[11 empty] | DS-1 |  | RR:
SH(s):
jk (s):
[11 empty] | DS-3 |  | RR:
| Do the Return Cable Tags have both Near and Far End information? | [9 empty] | SH(s):
jk (s):
| Fiber |  | RR (s):
| SH(s): |  |  |  | prt:
Cable Name:
Cable Count/ckt:
| Timing |  |  |  |  | Alarms |  | RR: |  |  |  | Network Alarming |  |  | RR:
| RR: |  |  |  |  | ETEL | [5 empty] | X.25, CO-LAN, NNET
| CNTL/RMT/EXPN |  |  |  |  | Upper / Lower | [5 empty] | SH:
| (card X tap) Pri: |  |  |  |  | Equip PNL: | [5 empty] | Slot:
| (card X tap)Sec: |  |  |  |  | Link/Port/Term: | [5 empty] | Link/Port:
Note on F12: Fans should be labeled: (FAN01, FAN02 etc)
Note on M12: Fans should be labeled: (FAN01, FAN02 etc)
Note on T12: Fans should be labeled: (FAN01, FAN02 etc)
Note on AA12: Fans should be labeled: (FAN01, FAN02 etc)
Note on B20: Choose Power Bay Type from drop down menu: PBD= Power Board Distribution BDFB= Battery Distribution Fuse Board BDCBB= Battery Distribution Circuit Breaker Board RING= Ring Plant -130V= Neg 130 volt Plant +130V= Pos 130 volt Plant Battery String
Note on E20: Example: P0123.01
Note on H20: Example: LD-A, LD-A1, LD-B etc. Or Battery String designation: A-Z, AA-ZZ (do not use I ,O)
Note on H38: add shelf designation number here. Ex: 04-01 (for EXPN 04-1)
Note on F39: example card - tap: 3 X 1
Note on F40: example card - tap: 4 X 1

## EMG Completion Checklist
EMG-INSTALLATION COMPLETION CHECKLIST
BVAPP | 0 |  | Job | 0 |  | Engineer |  | 0 |  | Phone Number | 0
Installation Representative |  | 0 |  | Lead Installer |  | 0 |  | Contact Number |  | 0
Electrical Vendor | 0 |  |  | Lead Electrician |  | 0 |  | Contact Number |  | 0
DATES | Actual Start |  | 0 |  | Walkthrough |  | 0 |  | Completion |  | 0
Job description of equipment added/removed | 0
Equipment added, modified, removed location(s) | :
(1) RR/Cabinet RR: | 0 | Fuse Panels | 0 | Fiber Shelves | 0 |  | Equip Shelves | 0 | Fans | 0
(2) RR/Cabinet RR: | 0 | Fuse Panels | 0 | Fiber Shelves | 0 |  | Equip Shelves | 0 | Fans | 0
(3) RR/Cabinet RR: | 0 | Fuse Panels | 0 | Fiber Shelves | 0 |  | Equip Shelves | 0 | Fans | 0
(4) RR/Cabinet RR: | 0 | Fuse Panels | 0 | Fiber Shelves | 0 |  | Equip Shelves | 0 | Fans | 0
Power | 0 | 0 |  | Panel | 0 | FS Position | 0 | Fuse/Breaker size |  | A
Power | 0 | 0 |  | Panel | 0 | FS Position | 0 | Fuse/Breaker size |  | A
Power | 0 | 0 |  | Panel | 0 | FS Position | 0 | Fuse/Breaker size |  | A
Power | 0 | 0 |  | Panel | 0 | FS Position | 0 | Fuse/Breaker size |  | A
Power | 0 | 0 |  | Panel | 0 | FS Position | 0 | Fuse/Breaker size |  | A
Power | 0 | 0 |  | Panel | 0 | FS Position | 0 | Fuse/Breaker size |  | A
DSO | Frame | 0 |  | Horizontal | 0 |  |  | Vertical |  | 0
DS1 | Relay Rack | 0 |  | Shelves | 0 |  | JACKS | 0
DS3 | Relay Rack | 0 |  | Shelves | 0 |  | JACKS | 0
FIBER | Relay Rack | 0 | Shelves | 0 | PORTS | 0 |  | Cable Name | 0 | Count | 0
TIMING | Relay Rack | 0 | RMT/EXPN/CNTL |  |  | Primary | 0 | Secondary | 0
ALARMS | Relay Rack | 0 | ETEL | 0 | Equipment Panel |  | E | Line/Port/Term |  | 0
Net Alarm- | Relay Rack | 0 | Shelves | 0 |  | SLOT | 0 |  | Line/Port | 0
CHECKLIST | YES | NO | INSTALLATION & THE CENTRAL OFFICE REPRESENTATIVE TO VERIFY THE FOLLOWING
Labeling and Stickmap information matches for all fields required.
All cabling is correctly secured at all break offs and & other required securing areas.
All cabling is protected where required. All fiber cabling is protected at all securing locations.
Amphenol cabling is secure and labeled where they can be removed and re-installed incorrectly.
Terminations are secure. (Power, Ground, Amphenol, Coax, Wire wrap, etc.)
Cards, Modules, and Fiber jumpers are highlighted on the BOM and received.
Tools, Vender owned material & job related paperwork is removed. Trash and cardboard removed daily.
All excess & scrap material has been disposed of properly per CenturyLink requirements.
Central Office Representative | [6 empty] | Contact Number
Installation Representative | [6 empty] | Contact Number
CPA or Supervisor | [6 empty] | Contact Number
Notes