Contents

6. 	 Cable Rack and Auxiliary Framing-	7

6C 	 Auxiliary Framing - High Type	7

6C.1 	 General	7

6C.2 	 Ceiling Heights	8

6C.3 	 Fastening Arrangements at Ceilings	8

6C.4 	 Hanger Rods	9

6C.5 	 Engineering Requirements	9

6C.6 	 Bracing – Light Earthquake Zone	10

EXHIBITS

2-E3-1	 BEAM CLAMP	11

2-E3-2	 CEILING INSERT AS INSTALLED	11

2-E3-3	 EXPANSION ANCHOR FOR HANGER ROD	12

2-E3-4	 HANGER BOLTS USED WHERE BEAM CLAMPS OR EMBEDDED CEILING INSERTS ARE NOT PROVIDED	12

2-E3-5	 (A&M) TYPICAL LAYOUT OF BEAM CLAMPS, ATTACHMENT POINTS, OR INSERTS AND PRIMARY BARS OR CHANNELS	13

2-E3-6	 HANGER ROD ATTACHED TO BEAM CLAMP OR CEILING INSERT	14

2-E3-6A	 HANGER ROD PASSING THROUGH FALSE CEILING	14

2-E3-6B	 FASTENING CEILING HANGER ROD TO EMBEDDED CEILING CHANNEL	15

2-E3-6C	 FASTENING AUXILIARY FRAMING BRACE TO EMBEDDED CEILING CHANNEL	15

2-E3-6D	 FASTENING CEILING HANGER ROD TO CEILING MOUNTED CHANNEL	16

2-E3-7	 DOUBLE-LEVEL BARS OR CHANNELS ATTACHED WITH A BOLT ASSEMBLY	17

2-E3-8	 (A&M) DOUBLE-LEVEL AUXILIARY FRAMING-SINGLE BARS ATTACHED TO DOUBLE BARS OR CHANNELS	17

2-E3-9	 SINGLE-LEVEL AUXILIARY FRAMING INTERSECTION OF BARS OR CHANNELS	18

2-E3-10	 SINGLE-LEVEL AUXILIARY FRAMING JUNCTION OF BARS OR CHANNELS	19

2-E3-11	 SINGLE LEVEL BARS OR CHANNELS ATTACHED TO HANGER RODS	20

2-E3-11A	 DOUBLE LEVEL BARS OR CHANNELS ATTACHED TO HANGER   RODS	20

2-E3-12	 DOUBLE FRAMING ATTACHED TO WALLS WHERE IMPRACTICABLE TO DRILL WALL ANGLE	21

2-E3-12A	 (A&M) SEE 2-E2-8C DOUBLE FRAMING ATTACHED TO WALLS WHERE ANGLE IS DRILLED	22

2-E3-13	 (A&M) SINGLE FRAMING ATTACHED TO WALLS	23

2-E3-14	 HANGER RODS OR BOLTS ATTACHED AT ENDS OF DOUBLE BARS OR CHANNELS	24

2-E3-15	 BRACING UPPER LEVEL FRAMING	24

2-E3-16	 BRACING LOWER LEVEL FRAMING AT RIGHT ANGLES TO HIGHER LEVEL FRAMING	25

2-E3-16A	 BRACING LOWER LEVEL FRAMING PARALLEL TO HIGHER LEVEL FRAMING	26

2-E3-17	 ATTACHING DOUBLE BRACING	27

2-E3-18	 TYPICAL LAYOUT OF BRACING DETAILS FOR PRIMARY FRAMING BARS OR CHANNELS	28

2-E3-19	 (DISCONTINUED) SPLICING SINGLE 2 INCHES BY 3/8 OF AN INCH BARS TO 2 INCHES BY 1/2 OF AN INCH BARS	29

2-E3-20	 (A&M) SPLICING PAIRS OF 2 INCHES BY 3/8 OF AN INCH BARS TO 2 INCHES BY 1/2 OF AN INCH BARS	30

2-E3-20A	 (A&M) SPLICING PAIRS OF 2 INCHES BY 3/8 OF AN INCH OR 2 INCHES BY 1/2 OF AN INCH BARS TO CHANNELS	31

2-E3-21	 SPLICING PAIRS OF 2 INCHES BY 3/8 OF AN INCH BARS	32

2-E3-21A	 SPLICING PAIRS OF 2 INCHES BY 9/16 OF AN INCH CHANNELS	32

2-E3-22	 (DISCONTINUED) DOUBLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS AT RIGHT ANGLES TO BEAMS OR GIRDERS	33

2-E3-22A	 DOUBLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS AT RIGHT ANGLES TO BEAMS OR GIRDERS	34

2-E3-23	 (DISCONTINUED) DOUBLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS PARALLEL TO BEAMS OR GIRDERS	35

2-E3-23A	 DOUBLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS PARALLEL TO BEAMS OR GIRDERS	36

2-E3-24	 (DISCONTINUED) SINGLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY	37

2-E3-25	 (DISCONTINUED) SINGLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS AT RIGHT ANGLES TO BEAMS OR GIRDERS	37

2-E3-26	 (DISCONTINUED) SUPPORTING FRAMING WHERE HANGER RODS INTERFERE WITH OTHER ATTACHMENTS	38

2-E3-27	 (DISCONTINUED) FRAMING BARS OR CHANNELS ATTACHED AT FRAME SUPPORTS-MAIN HANGER ROD AT POINT OF SUPPORT	38

2-E3-28	 CABLE RACK OR CONDUIT HANGER RODS ATTACHED TO FRAMING - CABLE RACK OR CONDUIT RUN AT RIGHT ANGLES TO PRIMARY BARS OR CHANNELS	39

2-E3-29	 CABLE RACK OR CONDUIT HANGER RODS ATTACHED TO FRAMING - CABLE RACK OR CONDUIT RUN PARALLEL TO PRIMARY BARS OR CHANNELS	39

2-E3-35	 (A&M) SINGLE BRACE FRAME SUPPORT	40

2-E3-36	 (A&M) DOUBLE BRACE FRAME SUPPORT USING THREADED ROD BRACES	41

2-E3-36A	 (A&M) DOUBLE BRACE FRAME SUPPORT USING ANGLE-TYPE BRACES	42

2-E3-37	 (DISCONTINUED) BRACE AT HANGER ROD	43

2-E3-38	 BRACE ATTACHED AT JUNCTION OF FRAMING BARS OR   CHANNELS	43

2-E3-44	 (DISCONTINUED) V BAR FRAME SUPPORT FOR FRAMES WITH SINGLE TOP ANGLES	44

2-E3-44A	 (DISCONTINUED) V BAR FRAME SUPPORT FOR BULB ANGLE TYPE FRAMES	44

TABLES

TABLE 6C.1  BRACING BETWEEN AUXILIARY FRAMING LEVELS IN A LIGHT EARTHQUAKE ZONE	12

# 6. 		Cable Rack and Auxiliary Framing-

## 6C 		Auxiliary Framing - High Type

## 6C.1 		General

This heading contains the general engineering requirements for ceiling suspended auxiliary framing. Refer to the chapter on low type framing for auxiliary framing over line-ups of transmission and power equipment.

- Refer to the "Auxiliary Framing - Low Type" section for auxiliary framing "Description" and "General Engineering Requirements".

- Refer to the "Earthquake and Disaster Bracing" section for auxiliary framing requirements for earthquake heavy zones.

  - Refer to these requirements where multiple levels of framing are used between the ceiling and the top of framework for framing used to support main aisle cable racking via cable rack support.

  - 1.	between the ceiling and the top of framework

  - 2.	for framing used to support main aisle cable racking

  - 3.	via cable rack support.

Safe load limitations for u-channel, embedded ceiling inserts, expansion anchors, hanger rods, and auxiliary framing are covered in the unit on Cable Rack Requirements.

Auxiliary framing shall be provided for support of equipment, cable racks, frame lighting and other apparatus in the Network Facility.

- Framing parts shall be directly butted. All measurements shown in Exhibits indicate maximum allowable gap tolerances.

Self-drilling anchors shall not be used to secure frames or secure ironwork to ceilings, walls or floors.

- Substitute appropriate lag bolts for attaching frames or ironwork to wooden ceilings, walls, or floors.

- Substitute torque-indicating anchors where embedded inserts or expansion anchors are shown.

Auxiliary framing arrangements not specifically identified in this document shall adhere to the intent of the requirements and guidelines.

Bolting details shall be installed as illustrated in the Exhibits.

Refer to CenturyLink Technical Documents and Standard Configurations for additional information. Standard Configurations may include essential information, specific arrangements, approved products, or direction on applying engineering requirements.

## 6C.2 		Ceiling Heights

The location and arrangement of high type auxiliary framing is dependent on ceiling height and clearance from obstructions such as ceiling beams, HVAC duct, and building conduit.

### 6C.3 		Fastening Arrangements at Ceilings

Equipment areas are usually provided with embedded ceiling inserts, embedded ceiling channel, ceiling mounted u-channel, or other devices arranged for fastening auxiliary framing to the ceiling, as follows:

Continuous channel inserts are embedded in the concrete ceiling in parallel rows and extend over all the equipment area. Rows of channel inserts are usually spaced 5 feet to 6 feet apart.

- CenturyLink Real Estate shall be notified for any new ceiling supported cable rack layouts to ensure the structural integrity of the ceiling for the design weight load.

- Embedded ceiling inserts, beam clamps, or embedded ceiling channel are typically located over the floor space assigned for telephone equipment as shown in              Exhibit 2-E3-5.

- A commonly used beam clamp is shown in Exhibit 2-E3-1. The usual size clamp may be attached to beam flanges up to 15 inches in width. The sockets of the spindles of these clamps are tapped for 5/8"-11 threads.  Projects with ceiling support requiring the use of beam clamps shall notify Real Estate for review of the ceiling to determine the appropriate beam clamps required.

- An example of the embedded ceiling inserts is shown in Exhibit 2-E3-2. Where ironwork will be engineered to be supported from ceiling inserts, an auxiliary framing grid is required near the ceiling. The initial grid should be engineered close enough to the ceiling so that bracing is not required.

- Fastening threaded hanger rods or ceiling braces as shown in Exhibit 2-E3-6B, or 6C, or 6D.

CenturyLink approved anchors may be used for hanger rods, braces, and similar occasional ceiling attachments in areas not supplied with embedded ceiling inserts or u-channel.

- The 5/8"-11 expansion anchor, as shown in Exhibit 2-E3-3, shall be used for such attachments.

Hanger bolts, as shown in Exhibit 2-E3-4, are occasionally used to support heavy loads where other building attachments have not been provided.

The addition of ceiling mounted u-channel, expansion anchors, etc., for attachments to ceilings is requested through Corporate Real Estate.

## 6C.4 		Hanger Rods

Hanger rods (threaded rods) used for the support of auxiliary framing and cable rack shall be 5/8"-11 and threaded the entire length of the rod.

HANGER RODS ATTACHED AT CEILINGS:

- Support from embedded ceiling inserts, beam clamps, or expansion anchors as shown in Exhibits 2-E3-3 and 2-E3-6.

- A 5/8"-11 hex nut and 1-3/4 inch washer, as shown in Exhibits 2-E3-3, 4, and 6, shall be used at the ceiling on all hanger rods and bolts, regardless of the type of finish on the ceiling or the kind or support,

- Where false or suspended ceilings are encountered, an additional 1-3/4 inch washer and two 5/8"-11 nuts shall be used on each rod. The washer shall be placed below the ceiling with one nut to hold it in place against the ceiling and the other to serve as a locknut as shown in Exhibit 2-E3-6A.

- Where u-channel is attached to a ceiling or suspended for other support purposes, a u-channel clip and 5/8"-11 nut shall be used on each rod as shown in Exhibit 2-E3-6D.

- When used with beam clamps, threaded rods shall be screwed into beam clamps until firmly seated, then backed away approximately one full turn to prevent binding, after which the locknut at the ceiling shall be tightened.

SPLICING HANGER RODS:

- Hanger rods or threaded rods used for braces shall not be spliced.

## 6C.5 		Engineering Requirements

Space required for access, adding, or removing equipment, vent ducts, ironwork, conduit, etc shall be taken into consideration when determining locations of auxiliary framing and supports.

Double-level auxiliary framing, consisting of primary and secondary channel, shall be used in areas where high framing is specified.

- Primary and secondary bars or channels shall be spaced approximately 5 feet apart. In no case shall the spacing exceed 6 feet apart.  Auxiliary framing supports spaced greater than 5 feet in one direction should be placed less than 5 feet in the perpendicular direction to maintain the maximum allowable loading.  As a general rule, the total square feet of the auxiliary framing supports shall not exceed 25 square feet (ie. 5’6” in one direction would require supports placed in approximately 4’6” in the perpendicular direction).

- Cable racking sized at 25 inches or greater and requiring auxiliary framing support may require spacing of auxiliary framing closer than 5 feet intervals.

- Single level framing bars shall be supported as shown in Exhibit 2-E3-11.

- Secondary framing shall be installed beneath and at right angles to the primary framing to add stiffening per Exhibit 2-E3-7 or 2-E3-11A. Where ladder type cable rack will be used as stiffening, secondary framing may be omitted.

Auxiliary framing shall be installed in accordance with Exhibits 2-E3-28 and 2-E3-29 where additional auxiliary framing is required for the support of cable racks and conduit.

Single-level auxiliary framing utilizing Exhibits 2-E3-9 and 2-E3-10 may be used in ceiling supported environments where additional space over head is required or where needed to provide required cable rack support where space is a concern.

Clips used for auxiliary framing assemblies are 1-7/8 inches wide. Where bar type framing is encountered, 1-1/2 inch wide framing clips shall be used.

Where bars or channels terminate at hanger rods, they shall be supported as shown in Exhibit 2-E3-14.

Auxiliary framing shall be provided under beams or girders, where required, per Exhibits 2-E3-22A and 2-E3-23A.

Auxiliary framing shall be located as high as practicable above Distributing Frames (DF) to provide cabling clearance and headroom.

JUNCTIONING AUXILIARY FRAMING: Where junctioning auxiliary framing is necessary, junctions shall be made as follows:

- Channels shall be junctioned together as shown in Exhibit 2-E3-21A.

- The 2 by 3/8 inches bars or 2 by 1/2 inches bars shall be junctioned to channels as shown in Exhibit 2-E3-20A.

- (A&M) The 2 inches by 3/8-inch bars shall be junctioned to 2 inches by 1/2-inch bars when extending old high-type framing installations as shown in Exhibits 2-E3-19 and 2-E3-20. Clamp junctions as shown in Exhibit 2-E3-21 shall be used where 2 by 3/8 inches bars are junctioned together either in pairs or singularly.

## 6C.6 		Bracing – Light Earthquake Zone

The entire ceiling supported auxiliary framing structure shall be braced similar to Exhibit 2-E2-2E with ceiling braces of the threaded rod or angle type.

- The braces shall be located at approximate building column intervals or about 20 feet in both directions in a building not having columns.

- A brace shall be provided within 10 feet of the last support of an auxiliary framing course. An auxiliary framing course is a succession of channels junctioned end-to-end.

- Both primary and secondary framing shall be braced per the table listed below.

Framing bars or channels shall be braced per the distances in the following table and where necessary to provide rigidity for framing that supports cable rack.

TABLE 6C.1  BRACING BETWEEN AUXILIARY FRAMING LEVELS IN A LIGHT EARTHQUAKE ZONE

| DISTANCE TO CEILING OR BETWEEN AUXILIARY FRAMING LEVELS | TYPE OF BRACE | EXHIBIT |
| --- | --- | --- |
| Less than 1 foot 0 inches | Not Required | N/A |
| 1 foot 0 inches to 2 foot 6 inches | Single-rod brace | 2-E3-15, 16, 16A, 18 |
| Over 2 foot 6 inches | Double-rod brace | 2-E3-17, 18 |

- The maximum distance between levels of framing or the ceiling and the first level of framing shall not exceed 5 feet 0 inches.

- Where lower level framing bars or channels are used only for the support of cable racks, bracing shall be furnished only as required for rigidity of the cable racks.

Braces shall be attached to hanger rods specifically as illustrated by bracing Exhibits.

EXHIBIT 2-E3-1

2-E3-1		BEAM CLAMP

EXHIBIT 2-E3-2

2-E3-2		CEILING INSERT AS INSTALLED

EXHIBIT 2-E3-3

2-E3-3		EXPANSION ANCHOR FOR HANGER ROD

EXHIBIT 2-E3-4

2-E3-4		HANGER BOLTS USED WHERE BEAM CLAMPS OR EMBEDDED CEILING INSERTS ARE NOT PROVIDED

EXHIBIT 2-E3-5 (A&M)

2-E3-5		(A&M) TYPICAL LAYOUT OF BEAM CLAMPS, ATTACHMENT POINTS, OR INSERTS AND PRIMARY BARS OR CHANNELS

EXHIBIT 2-E3-6

2-E3-6		HANGER ROD ATTACHED TO BEAM CLAMP OR CEILING INSERT

EXHIBIT 2-E3-6A

2-E3-6A		HANGER ROD PASSING THROUGH FALSE CEILING

EXHIBIT 2-E3-6B

2-E3-6B		FASTENING CEILING HANGER ROD TO EMBEDDED CEILING CHANNEL

EXHIBIT 2-E3-6C

2-E3-6C		FASTENING AUXILIARY FRAMING BRACE TO EMBEDDED CEILING CHANNEL

EXHIBIT 2-E3-6D

2-E3-6D		FASTENING CEILING HANGER ROD TO CEILING MOUNTED CHANNEL

EXHIBIT 2-E3-7

2-E3-7		DOUBLE-LEVEL BARS OR CHANNELS ATTACHED WITH A BOLT ASSEMBLY

EXHIBIT 2-E3-8 (A&M)

2-E3-8		(A&M) DOUBLE-LEVEL AUXILIARY FRAMING-SINGLE BARS ATTACHED TO DOUBLE BARS OR CHANNELS

EXHIBIT 2-E3-9

2-E3-9		SINGLE-LEVEL AUXILIARY FRAMING INTERSECTION OF BARS OR CHANNELS

EXHIBIT 2-E3-10

2-E3-10		SINGLE-LEVEL AUXILIARY FRAMING JUNCTION OF BARS OR CHANNELS

EXHIBIT 2-E3-11

2-E3-11		SINGLE LEVEL BARS OR CHANNELS ATTACHED TO HANGER RODS

EXHIBIT 2-E3-11A

2-E3-11A		DOUBLE LEVEL BARS OR CHANNELS ATTACHED TO HANGER RODS

EXHIBIT 2-E3-12

2-E3-12		DOUBLE FRAMING ATTACHED TO WALLS WHERE IMPRACTICABLE TO DRILL WALL ANGLE

EXHIBIT 2-E3-12A (A&M) SEE 2-E2-8C

2-E3-12A		(A&M) SEE 2-E2-8C DOUBLE FRAMING ATTACHED TO WALLS WHERE ANGLE IS DRILLED

EXHIBIT 2-E3-13 (A&M)

2-E3-13		(A&M) SINGLE FRAMING ATTACHED TO WALLS

EXHIBIT 2-E3-14

2-E3-14		HANGER RODS OR BOLTS ATTACHED AT ENDS OF DOUBLE BARS OR CHANNELS

EXHIBIT 2-E3-15

2-E3-15		BRACING UPPER LEVEL FRAMING

EXHIBIT 2-E3-16

2-E3-16		BRACING LOWER LEVEL FRAMING AT RIGHT ANGLES TO HIGHER LEVEL FRAMING

EXHIBIT 2-E3-16A

2-E3-16A		BRACING LOWER LEVEL FRAMING PARALLEL TO HIGHER LEVEL FRAMING

EXHIBIT 2-E3-17

2-E3-17		ATTACHING DOUBLE BRACING

EXHIBIT 2-E3-18

2-E3-18		TYPICAL LAYOUT OF BRACING DETAILS FOR PRIMARY FRAMING BARS OR CHANNELS

EXHIBIT 2-E3-19 (DISCONTINUED)

2-E3-19		(DISCONTINUED) SPLICING SINGLE 2 INCHES BY 3/8 OF AN INCH BARS TO 2 INCHES BY 1/2 OF AN INCH BARS

EXHIBIT 2-E3-20 (A&M)

2-E3-20		(A&M) SPLICING PAIRS OF 2 INCHES BY 3/8 OF AN INCH BARS TO 2 INCHES BY 1/2 OF AN INCH BARS

EXHIBIT 2-E3-20A (A&M)

2-E3-20A		(A&M) SPLICING PAIRS OF 2 INCHES BY 3/8 OF AN INCH OR 2 INCHES BY 1/2 OF AN INCH BARS TO CHANNELS

EXHIBIT 2-E3-21

2-E3-21		SPLICING PAIRS OF 2 INCHES BY 3/8 OF AN INCH BARS

EXHIBIT 2-E3-21A (A&M)

2-E3-21A		SPLICING PAIRS OF 2 INCHES BY 9/16 OF AN INCH CHANNELS

EXHIBIT 2-E3-22 (DISCONTINUED)

2-E3-22		(DISCONTINUED) DOUBLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS AT RIGHT ANGLES TO BEAMS OR GIRDERS

EXHIBIT 2-E3-22A

2-E3-22A		DOUBLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS AT RIGHT ANGLES TO BEAMS OR GIRDERS

EXHIBIT 2-E3-23 (DISCONTINUED)

2-E3-23		(DISCONTINUED) DOUBLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS PARALLEL TO BEAMS OR GIRDERS

EXHIBIT 2-E3-23A

2-E3-23A		DOUBLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS PARALLEL TO BEAMS OR GIRDERS

EXHIBIT 2-E3-24 (DISCONTINUED)

2-E3-24		(DISCONTINUED) SINGLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY

EXHIBIT 2-E3-25 (DISCONTINUED)

2-E3-25		(DISCONTINUED) SINGLE FRAMING UNDER BEAMS OR GIRDERS-PRIMARY BARS OR CHANNELS AT RIGHT ANGLES TO BEAMS OR GIRDERS

EXHIBIT 2-E3-26 (DISCONTINUED)

2-E3-26		(DISCONTINUED) SUPPORTING FRAMING WHERE HANGER RODS INTERFERE WITH OTHER ATTACHMENTS

EXHIBIT 2-E3-27 (DISCONTINUED)

2-E3-27		(DISCONTINUED) FRAMING BARS OR CHANNELS ATTACHED AT FRAME SUPPORTS-MAIN HANGER ROD AT POINT OF SUPPORT

EXHIBIT 2-E3-28

2-E3-28		CABLE RACK OR CONDUIT HANGER RODS ATTACHED TO FRAMING - CABLE RACK OR CONDUIT RUN AT RIGHT ANGLES TO PRIMARY BARS OR CHANNELS

EXHIBIT 2-E3-29

2-E3-29		CABLE RACK OR CONDUIT HANGER RODS ATTACHED TO FRAMING - CABLE RACK OR CONDUIT RUN PARALLEL TO PRIMARY BARS OR CHANNELS

EXHIBIT 2-E3-35 (A&M)

2-E3-35		(A&M) SINGLE BRACE FRAME SUPPORT

EXHIBIT 2-E3-36 (A&M)

2-E3-36		(A&M) DOUBLE BRACE FRAME SUPPORT USING THREADED ROD BRACES

EXHIBIT 2-E3-36A (A&M)

2-E3-36A		(A&M) DOUBLE BRACE FRAME SUPPORT USING ANGLE-TYPE BRACES

EXHIBIT 2-E3-37 (DISCONTINUED)

2-E3-37		(DISCONTINUED) BRACE AT HANGER ROD

EXHIBIT 2-E3-38

2-E3-38		BRACE ATTACHED AT JUNCTION OF FRAMING BARS OR CHANNELS

EXHIBIT 2-E3-44 (DISCONTINUED)

2-E3-44		(DISCONTINUED) V BAR FRAME SUPPORT FOR FRAMES WITH SINGLE TOP ANGLES

EXHIBIT 2-E3-44A (DISCONTINUED)

2-E3-44A		(DISCONTINUED) V BAR FRAME SUPPORT FOR BULB ANGLE TYPE FRAMES